NAESB TLR Standard – Version 0 Draft 1

NAESB Transmission Loading Relief Standard

Version 0

1. General Requirements

1.1. Initiation only by Reliability Authority. A Reliability Authority shall be the only entity authorized to initiate the NAESB Transmission Loading Relief Procedure and shall do so at 1) the Reliability Authority’s own request, or 2) upon the request of a Transmission Operator.
1.2. Mitigating transmission constraints. A Reliability Authority shall utilize the TLR Procedure to mitigate potential or actual System Operating Limit Violations or Interconnection Reliability Operating Limit violations on any transmission facility modeled in the Interchange Distribution Calculator. 
1.2.1. Requesting relief on tie facilities. Any Transmission Operator who operates the tie facility shall be allowed to request relief from its Reliability Authority.

1.2.1.1. Interchange Transaction priority on tie facilities. The priority of the Interchange Transaction(s) to be curtailed shall be determined by the Transmission Service reserved on the Transmission Service Provider’s system who requested the relief.

1.3. Order of TLR Levels and taking emergency action. The Reliability Authority shall not be required to follow the TLR Levels in their numerical order (Requirement 2, “TLR Levels”). Furthermore, if a Reliability Authority deems that a transmission loading condition could jeopardize bulk system reliability, the Reliability Authority shall have the authority to enter TLR Level 6 directly, and immediately direct the Balancing Authorities or Transmission Operators to take such actions as re-dispatch generation, or reconfigure transmission, or reduce load to mitigate the critical condition until Interchange Transactions can be reduced utilizing the TLR Transaction Curtailment Procedures, or other methods, to return the system to a secure state.

1.4. Notification of TLR Procedure implementation. The Reliability Authority initiating the use of the TLR Procedure shall notify other Reliability Authorities and Balancing Authorities and Transmission Operators, and must post the initiation and progress of the TLR event on the appropriate NERC web page(s).

1.4.1. Notifying other Reliability Authorities. The Reliability Authority initiating the TLR Procedure shall inform all other Reliability Authorities via the Reliability Authority Information System (RAIS) that the TLR Procedure has been implemented.

1.4.1.1. Actions expected. The Reliability Authority initiating the TLR Procedure shall indicate the actions expected to be taken by other Reliability Authorities. 
1.4.2. Notifying Transmission Operators and Balancing Authorities. Reliability Authorities shall notify Transmission Operators and Balancing Authorities in his Reliability Area when entering and leaving any TLR level.

1.4.3. Notifying Balancing Authorities. The Reliability Authority for the Sink Balancing Authority shall be responsible for directing the sink Balancing Authority to curtail the Interchange Transactions as specified by the Reliability Authority implementing the TLR Procedure. 
1.4.3.1. Notification order. Within a Transmission Service priority level, the Sink Balancing Authorities whose Interchange Transactions have the largest impact on the Constrained Facilities shall be notified first if practicable.

1.4.4. Updates. At least once each hour, or when conditions change, the Reliability Authority implementing the TLR Procedure shall update all other Reliability Authorities (via the RAIS). Transmission Operators and Balancing Authorities who have had Interchange Transactions impacted by the TLR will be updated by their Reliability Authority. 
1.5. Obligations. All Reliability Authorities shall comply with the request of the Reliability Authority who initiated the TLR Procedure, unless the initiating Reliability Authority agrees otherwise.

1.5.1. Use of TLR Procedure with “local” procedures. A Reliability Authority shall be allowed to implement a local transmission loading relief or congestion management procedure simultaneously with an Interconnection-wide procedure. However, the Reliability Authority shall be obligated to follow the curtailments as directed by the Interconnection-wide procedure. If the Reliability Authority desires to use a local procedure as a substitute for curtailments as directed by the Interconnection-wide procedure, he may do so only if such use is approved by the NERC Operating Reliability Subcommittee and Operating Committee.

1.6. Consideration of Interchange Transactions. The administration of the TLR Procedure shall be guided by information obtained from the Interchange Distribution Calculator (IDC). 

1.6.1. Interchange Transactions not in the IDC. Reliability Authorities shall also treat known Interchange Transactions that may not appear in the IDC in accordance with the procedures in this document.

1.6.2. Transmission elements not in IDC. When a Reliability Authority is faced with an overload on a transmission element that is not modeled in the IDC, the Reliability Authority shall use the best information available to curtail Interchange Transactions in order to operate the system in a reliable manner. The Reliability Authority shall use his best efforts to ensure that Interchange Transactions with a Transfer Distribution Factor of less than the Curtailment Threshold on the transmission element not modeled in the IDC are not curtailed.

1.6.3. Questionable IDC results. Any Reliability Authority (or Transmission Operator through his Reliability Authority) who believes the curtailment list from the IDC for a particular TLR event is incorrect shall use his best efforts to communicate those adjustments necessary to bring the curtailment list into conformance with the principles of this Procedure to the initiating Reliability Authority. Causes of questionable IDC results may include:

· Missing Interchange Transactions that are known to contribute to the Constraint.

· Significant change in transmission system topology

· TDF matrix error.

Impacts of questionable IDC results may include:

· Curtailment that would have no effect on, or aggravate the constraint.

· Curtailment that would initiate a constraint elsewhere.

If other Reliability Authorities are involved in the TLR event, all impacted Reliability Authorities shall be in agreement before any adjustments to the curtailment list are made.

1.6.4. Curtailment that would cause a constraint elsewhere. The Reliability Authority shall be allowed to exempt an Interchange Transaction from curtailment if the Reliability Authority is aware that the Interchange Transaction curtailment directed by the IDC would cause a constraint to occur elsewhere if the Reliability Authority has consulted with those Reliability Authorities who initiated the curtailment. 
1.6.5. Re-dispatch options. The Reliability Authority shall ensure that Interchange Transactions that are linked to re-dispatch options are protected from curtailment in accordance with the re-dispatch provisions. 
1.6.6. Reallocation.  The Reliability Authority shall consider for Reallocation any Transactions of higher priority that meet the Approved-tag Submission Deadline during a TLR Level 3A. The Reliability Authority shall consider for Reallocation any Transaction using Firm Transmission Service that has met the Approved-tag Submission Deadline during a TLR Level 5A,
1.9. IDC updates. Any Interchange Transaction adjustments or curtailments that result from using this Procedure must be entered into the common interconnection model (i.e. the IDC).
1.10. Logging. The Reliability Authority shall complete the NERC Transmission Loading Relief Procedure Log  whenever he invokes TLR Level 2 or above, and send a copy of the log via e-mail to the NERC staff within two business days of the TLR event. The staff shall post these logs on the NERC web site upon receipt.

1.11. TLR Event Review. The Reliability Authority shall report the TLR event to the NERC Market Committee and Operating Reliability Subcommittee in accordance with TLR review processes established by NERC as required. 

1.9.1. Providing information. Transmission Operators and Balancing Authorities within the Reliability Authority’s Reliability Area, and all other Reliability Authorities, including Transmission Operators and Balancing Authorities within their respective Reliability Areas, shall provide information, as requested by the initiating Reliability Authority, in accordance with TLR review processes established by NERC.

1.9.2. Market Committee reviews. The Market Committee may conduct reviews of certain TLR events based on the size and number of Interchange Transactions that are affected, the frequency that the TLR Procedure is called for a particular Constrained Facility, or other factors. 
1.9.3. Operating Reliability Subcommittee reviews. The Operating Reliability Subcommittee shall conduct reviews to ensure proper implementation and for “lessons learned”.
2. Transmission Loading Relief (TLR) Levels

Introduction

This section describes the various levels of the TLR Procedure. The description of each level begins with the circumstances that define the TLR Level, followed by the procedures to be followed.

The decision that a Reliability Authority makes in selecting a particular TLR Level often depends on the transmission loading condition and whether the Interchange Transaction is using Non-firm Point-to-Point Transmission Service or Firm Point-to-Point Transmission Service. There are further considerations that depend on whether the Constrained Facility is on or off the contract path. It is important to note that an Interchange Transaction using Firm Point-to-Point Transmission Service on all contract path links is considered a “firm” Interchange Transaction even if the Constrained Facility is off the contract path.

2.1. TLR Level 1 – Notify Reliability Authorities of potential System Operating Limit or Interconnection Reliability Operating Limit Violations.

2.1.1. The Reliability Authority shall use following circumstances to establish the need for TLR Level 1:

· The transmission system is secure.

· The Reliability Authority foresees a transmission or generation contingency or other operating problem within his Reliability Area that could cause one or more transmission facilities to approach or exceed their System Operating Limit or Interconnection Reliability Operating Limit.
2.1.2. Notification procedures. The Reliability Authority shall notify all Reliability Authorities via the Reliability Authority Information System as soon as the condition is foreseen. All affected Reliability Authorities shall check to ensure that Interchange Transactions are posted in the Interchange Distribution Calculator.

2.2. TLR Level 2 – Hold transfers at present level to prevent SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT Violations
2.2.1. The Reliability Authority shall use following circumstances to establish the need for entering TLR Level 2:

· The transmission system is secure,

· One or more transmission facilities are expected to approach, or are approaching, or are at their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT.

2.2.2. Holding procedures. The Reliability Authority shall be allowed to hold the implementation of any additional INTERCHANGE Transactions that are at or above the Curtailment Threshold.  However, the Reliability Authority should allow additional Interchange Transactions that flow across the Constrained Facility if their flow reduces the loading on the Constrained Facility or has a Transfer Distribution Factor less than the Curtailment Threshold. All Interchange Transactions using Firm Point-to-Point Transmission Service shall be allowed to start.

2.2.3. TLR Level 2 is a transient state, which requires a quick decision to proceed to higher TLR Levels (3 and above) to allow Interchange Transactions to be implemented according to their transmission reservation priority. The time for being in TLR Level 2 should be no more than 30 minutes, with the understanding that there may be circumstances where this time may be exceeded. If the time in TLR Level 2 exceeds 30 minutes, the Reliability Authority shall document this action on the TLR Log. 

2.3. TLR Level 3a – Reallocation of Transmission Service by curtailing Interchange Transactions using Non-firm Point-to-Point Transmission Service to allow Interchange Transactions using higher priority Transmission Service.

2.3.1. The Reliability Authority shall use following circumstances to establish the need for entering TLR Level 3a:

· The transmission system is secure

· One or more transmission facilities are expected to approach, or are approaching, or are at their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT
· Transactions using Non-firm Point-to-Point Transmission Service are flowing that are at or above the Curtailment Threshold on those facilities.

· The Transmission Provider has previously approved a higher priority Point-to-Point Transmission Service reservation over which a Transmission Customer wishes to begin an Interchange Transaction. 

2.3.2. Reallocation procedures to allow Interchange Transactions using higher priority Point-to-Point Transmission Service to start. The Reliability Authority with the constraint shall give preference to those Interchange Transactions using Firm Point-to-Point Transmission Service, followed by those using higher priority Non-firm Point-to-Point Transmission Service as specified in Requirement 3. “Interchange Transaction Curtailment Order.” Interchange Transactions that have been held or curtailed as prescribed in this Section shall be reallocated (reloaded) according to their Transmission Service priorities when operating conditions permit as specified in Requirement 6. “Interchange Transaction Reallocation During TLR Level 3a and 5a.”
2.3.2.1. The Reliability Authority shall displace Interchange Transactions with lower priority Transmission Service using Interchange Transactions having higher priority Non-firm or Firm Transmission Service.

2.3.2.2. The Reliability Authority shall not curtail Interchange Transactions using Non-firm Transmission Service to allow the start or increase of another Interchange Transaction having the same priority Non-firm Transmission Service. 

2.3.2.3. If there are insufficient Interchange Transactions using Non-firm Point-to-Point Transmission Service that can be curtailed to allow for Interchange Transactions using Firm Point-to-Point Transmission Service to begin, the Reliability Authority shall proceed to TLR Level 5a. 
2.3.2.4. The Reliability Authority shall reload curtailed Interchange Transactions prior to allowing the start of new or increased Interchange Transactions.

2.3.2.4.1. Interchange Transactions whose tags were submitted to the Tag Authority prior to the TLR Level 2 or Level 3a being called, but were subsequently held from starting, are considered to have been curtailed and thus would be reloaded the same time as the curtailed Interchange Transactions.

2.3.2.5. Transmission capability available for reloading or starting shall be filled by eligible Transactions on a pro-rata basis. (by whom?)
2.3.2.6. The Reliability Authority shall consider transactions whose tags meet the Approved-tag Submission Deadline for reallocation  for the upcoming hour. Tags submitted after this deadline shall be considered for reallocation the following hour.

2.4. TLR Level 3b – Curtail Interchange Transactions using Non-Firm Transmission Service Arrangements to mitigate a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT Violation

2.4.1. The Reliability Authority shall use following circumstances to establish the need for entering TLR Level 3b:
· One or more transmission facilities are operating above their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT, or

· Such operation is imminent and it is expected that facilities will exceed their security limit unless corrective action is taken, or

· One or more Transmission Facilities will exceed their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT upon the removal from service of a generating unit or another transmission facility

· Transactions using Non-firm Point-to-Point Transmission Service are flowing that are at or above the Curtailment Threshold on those facilities.

2.4.2. Holding new Interchange Transactions. The Reliability Authority shall hold all new Interchange Transactions using Non-firm Point-to-Point Transmission Service that are at or above the Curtailment Threshold during the period of the SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT Violation. The Reliability Authority shall allow Interchange Transactions using Firm Point-to-Point Transmission Service to start if they are submitted to the IDC within specific time limits as explained in Requirement 7. “Interchange Transaction Curtailments During TLR Level 3b.”
2.4.3. Curtailment procedures to mitigate an SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT. The Reliability Authority shall curtail Interchange Transactions using Non-firm Point-to-Point Transmission Service that are at or above the Curtailment Threshold as specified in Requirement 3. “Interchange Transaction Curtailment Order.”
2.5. TLR Level 4 – Reconfigure Transmission

2.5.1. The Reliability Authority shall use following circumstances to establish the need for entering TLR Level 4:
· One or more Transmission Facilities are above their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT, or

· Such operation is imminent and it is expected that facilities will exceed their security limit unless corrective action is taken

2.5.2. Holding new Interchange Transactions. The Reliability Authority shall hold all new Interchange Transactions using Non-firm Point-to-Point Transmission Service that are at or above the Curtailment Threshold during the period of the SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT Violation. The Reliability Authority shall allow Interchange Transactions using Firm Point-to-Point Transmission Service to start if they are submitted to the IDC by 00:25 or the time at which the TLR Level 4 is called, whichever is later.
2.5.3. Reconfiguration procedures. Following the curtailment of all Interchange Transactions using Non-firm Point-to-Point Transmission Service that are at or above the Curtailment Threshold in Level 3b that impact the Constrained Facilities, if a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT violation is imminent or occurring, the Reliability Authority(ies) shall request that the affected Transmission Operators reconfigure transmission on their system, or arrange for reconfiguration on other transmission systems, to mitigate the constraint. Specific details are explained in Requirement 4., “Principles for Mitigating Constraints On and Off the Contract Path”

2.6. TLR Level 5a – Reallocation of Transmission Service by curtailing Interchange Transactions using Firm Point-to-Point Transmission Service on a pro rata basis to allow additional Interchange Transactions using Firm Point-to-Point Transmission Service.

2.6.1. The Reliability Authority shall use following circumstances to establish the need for entering TLR Level 5a:

· The transmission system is secure

· One or more transmission facilities are at their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT
· All Interchange Transactions using Non-firm Point-to-Point Transmission Service that are at or above the Curtailment Threshold have been curtailed.

· The Transmission Provider has been requested to begin an Interchange Transaction using previously arranged Firm Transmission Service that would result in a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT Violation.

· No further transmission reconfiguration is possible or effective.

2.6.2. Reallocation procedures to allow new Interchange Transactions using Firm Point-to-Point Transmission Service to start. The Reliability Authority shall use the following three-step process for reallocation of Interchange Transactions using Firm Point-to-Point Transmission Service:

2.6.2.1. Step 1 – Identify available re-dispatch options. The Reliability Authority shall assist the Transmission Operator(s) in identifying those known re-dispatch options that are available to the Transmission Customer that will mitigate the loading on the Constrained Facilities. If such re-dispatch options are deemed insufficient to mitigate loading on the Constrained Facilities, the Reliability Authority shall proceed to implement these options while proceeding to Steps 2 and 3 below.

2.6.2.2. Step 2 – The Reliability Authority shall calculate the percent of the overload on the Constrained Facility caused by both Firm Point-to-Point Transmission Service (at or above the Curtailment Threshold) and the Transmission Provider’s Network Integration Transmission Service and Native Load, as required by the Transmission Provider’s filed tariff.  This is described in Requirement 5, “Parallel Flow Calculation Procedure for Reallocating or Curtailing Firm Transmission Service.”
2.6.2.3. Step 3 – Curtail Interchange Transactions using Firm Transmission Service. The Reliability Authority shall curtail or reallocate on a pro-rata basis (based on the MW level of the MW total to all such Interchange Transactions), those Interchange Transactions as calculated in Section 7.2.2 over the Constrained Facilities. (See also Requirement 6, “Interchange Transaction Reallocation During TLR 3a and 5a.” The Reliability Authority shall assist the Transmission Provider in curtailing Transmission Service to Network Integration Transmission Service customers and Native Load if such curtailments are required by the Transmission Provider’s tariff. Available re-dispatch options will continue to be implemented.

2.7. TLR Level 5b – Curtail Interchange Transactions using Firm Point-to-Point Transmission Service to mitigate a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT Violation.

2.7.1. The Reliability Authority shall use following circumstances to establish the need for entering TLR Level 5b:
· One or more Transmission Facilities are operating above their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT, or

· Such operation is imminent, or

· One or more Transmission Facilities will exceed their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT upon the removal from service of a generating unit or another transmission facility.

· All Interchange Transactions using Non-firm Point-to-Point Transmission Service that are at or above the Curtailment Threshold have been curtailed.

· No further transmission reconfiguration is possible or effective.

2.7.2. The Reliability Authority shall use the following three-step process for curtailment of Interchange Transactions using Firm Point-to-Point Transmission Service:

2.7.2.1. Step 1 – Identify available re-dispatch options. The Reliability Authority shall assist the Transmission Operators(s) in identifying those known re-dispatch options that are available to the Transmission Customer that will mitigate the loading on the Constrained Facilities. If such re-dispatch options are deemed insufficient to mitigate loading on the Constrained Facilities, the Reliability Authority shall proceed to implement these options while proceeding to Steps 2 and 3 below.

2.7.2.2. Step 2 – The Reliability Authority shall calculate the percent of the overload on the Constrained Facility caused by both, Firm Point-to-Point Transmission Service (at or above the Curtailment Threshold) and the Transmission Provider’s Network Integration Transmission Service and Native Load, as required by the Transmission Provider’s filed tariff.  This is described in Requirement 6, “Parallel Flow Calculation Procedure for Reallocating or Curtailing Firm Transmission Service.”
2.7.2.3. Step 3 – Curtailment of Interchange Transactions using Firm Transmission Service. At this point, the Reliability Authority shall begin the process of curtailing Interchange Transactions as calculated in Section 2.7.2.2 over the Constrained Facilities using Firm Point-to-Point Transmission Service until the SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT violation has been mitigated. The Reliability Authority shall assist the Transmission Provider in curtailing Transmission Service to Network Integration Transmission Service customers and Native Load if such curtailments are required by the Transmission Providers’ tariff. Available re-dispatch options will continue to be implemented.
2.8. TLR Level 6 – Emergency Procedures

2.8.1. The Reliability Authority shall use following circumstances to establish the need for entering TLR Level 6:
· One or more Transmission Facilities are above their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT.

· One or more Transmission Facilities will exceed their SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT upon the removal from service of a generating unit or another transmission facility.

2.8.2. Implementing emergency procedures. If the Reliability Authority deems that  SOL or IROL violations are imminent, the Reliability Authority shall immediately direct the Balancing Authorities and Transmission Operators in his Reliability Area to re-dispatch generation, or reconfigure transmission, or reduce load to mitigate the critical condition until Interchange Transactions can be reduced utilizing the TLR Procedures or other procedures to return the system to a secure state. All Balancing Authorities and Transmission Operators shall comply with all requests from their Reliability Authority.
2.9. TLR Level 0 – TLR concluded
2.9.1. Interchange Transaction restoration and notification procedures. The Reliability Authority initiating the TLR Procedure shall notify all Reliability Authorities within the Interconnection via the RAIS when the SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT violations are mitigated and the system is in a “normal” state, allowing Interchange Transactions to be reestablished at his discretion. Those with the highest transmission priorities shall be reestablished first if possible.
3. Interchange Transaction Curtailment Order

3.1. Priority of Interchange Transactions

3.1.1. Interchange Transaction curtailment priority shall be determined by the Transmission Service reserved over the constrained facility(ies) as follows:

Transmission Service Priorities

Priority 0.
Next-hour Market Service – NX*

Priority 1.
Service over secondary receipt and delivery points – NS

Priority 2.
Hourly Service – NH

Priority 3.
Daily Service – ND

Priority 4.
Weekly Service – NW

Priority 5.
Monthly Service – NM

Priority 6.
Network Integration Transmission Service from sources not designated as network resources – NN

Priority 7.
Firm Point-to-Point Transmission Service ( F and Network Integration Transmission Service from Designated Resources – FN
3.1.2. The curtailment priority for Interchange Transactions that do not have a Transmission Service reservation over the constrained facility(ies) shall be defined by the lowest priority of the individual reserved transmission segments.

3.2. Curtailment of Interchange Transactions Using Non-firm Transmission Service

3.2.1. The Reliability Authority shall direct the curtailment of Interchange Transactions using Non-firm Transmission Service that are at or above the Curtailment Threshold for the following TLR Levels:

3.2.1.1. TLR Level 3a. Enable Interchange Transactions using a higher Transmission reservation priority to be implemented, or

3.2.1.2. TLR Level 3b. Mitigate an SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT violation.

3.3. Curtailment of Interchange Transactions Using Firm Transmission Service

3.3.1. The Reliability Authority shall direct the curtailment of Interchange Transactions using Firm Transmission Service that are at or above the Curtailment Threshold for the following TLR Levels:

3.3.1.1. TLR Level 5a. Enable additional Interchange Transactions using Firm Point-to-Point Transmission Service to be implemented after all Interchange Transactions using Non-firm Point-to-Point Service have been curtailed, or

3.3.1.2. TLR Level 5b. Mitigate a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT violation that remains after all Interchange Transactions using Non-firm Transmission Service has been curtailed under TLR Level 3b, and following attempts to reconfigure transmission under TLR Level 4.

4. Mitigating Constraints On and Off the Contract Path

Introduction

Reserving transmission service for an Interchange Transaction along a “contract path” may not reflect the actual distribution of the power flows over the transmission network from generation source to load sink. Interchange Transactions arranged over a contract path may, therefore, overload transmission elements on other electrically parallel paths. The Reliability Authorities must agree on how the NERC Transmission Loading Relief Procedure will handle these Interchange Transactions to, first, ensure the operational security of the Interconnection and, second, respect the obligations of the Transmission Providers’ tariffs.

The curtailment priority of an Interchange Transaction depends on whether the Constrained Facility is on or off the contract path, and, if on the contract path, the Transmission Service of the link with the Constrained Facility.

The Reliability Authority must also consider 1) the tariff obligations of the Transmission Provider with the Constrained Facility, 2) the Transmission Customer’s re-dispatch or other congestion management arrangements, and 3) arrangements among the Transmission Providers for handling certain Constraints. 
4.1. Constraints ON the Contract Path

4.1.1. The Reliability Authority initiating TLR shall consider the entire Interchange Transaction non-firm if the transmission link on the Constrained Facility is Non-firm Point-to-Point Transmission Service,  even if other links in the contract path are firm. When the Constrained Facility is on the contract path, the Interchange Transaction takes on the transmission service priority of the Transmission Service link with the Constrained Facility regardless of the Transmission Service priority on the other links along the contract path.
4.1.1.1. Discussion. The Transmission Operator simply has to call its Reliability Authority, request the TLR Procedure be initiated, and allow the curtailments of all Interchange Transactions that are at or above the Curtailment Threshold to progress until the relief is realized. Firm Point-to-Point Transmission Service links elsewhere in the contract path do not obligate Transmission Providers providing Non-firm Point-to-Point Transmission Service to treat the transaction as firm. For curtailment purposes, the Interchange Transaction’s priority will be the priority of the Transmission Service link with the Constrained Facility. (See Requirement 4.1.2 below.)
4.1.2. The Reliability Authority initiating TLR shall consider the entire Interchange Transaction firm if the transmission link on the Constrained Facility is Firm Point-to-Point Transmission Service, even if other links in the contract path are non-firm. 
4.1.2.1. Discussion. The curtailment priority of an Interchange Transaction on a contract path link is not affected by the transmission service priorities arranged with other links on the contract path. If the Constrained Facility is on a Firm Point-to-Point Transmission Service contract path link, then the curtailment priority of the Interchange Transaction is considered firm regardless of the transmission service arrangements elsewhere on the contract path. If the Transmission Provider provides its services under the FERC pro forma tariff, it may also be obligated to offer its Transmission Customer alternate receipt and delivery points, thus allowing the Customer to curtail its Transmission Service over the Constrained Facilities.
4.2. Constraints OFF the Contract Path

4.2.1. The Reliability Authority initiating TLR shall consider the entire Interchange Transaction non-firm if non of the transmission links on the contract path are on the Constrained Facility and if any of the transmission links on the contract path are Non-firm Point-to-Point Transmission Service; the Interchange Transaction shall take on the lowest transmission service priority of all Transmission Service links along the contract path.
4.2.1.1. Discussion. An Interchange Transaction arranged over a contract path where one or more individual links consist of Non-firm Point-to-Point Transmission Service is considered to be a non-firm Interchange Transaction for Constrained Facilities off the contract path. Sufficient Interchange Transactions that are at or above the Curtailment Threshold will be curtailed before any Interchange Transactions using Firm Point-to-Point Transmission Service are curtailed. The priority level for curtailment purposes will be the lowest level of transmission service arranged for on the contract path.

4.2.2. The Reliability Authority initiating TLR shall consider the entire Interchange Transaction firm if all of the transmission links on the contract path are Firm Point-to-Point Transmission Service, even if non of the transmission links are on the Constrained Facility and shall not be curtailed to relieve a Constraint off the contract path until all non-firm Interchange Transactions that are at or above the Curtailment Threshold have been curtailed.
4.2.2.1. Discussion. If the entire contract path is Firm Point-to-Point Transmission Service, then the TLR procedure will treat the Interchange Transaction as firm even for Constraints off the contract path and will not curtail that Interchange Transaction until all non-firm Interchange Transactions that are at or above the Curtailment Threshold have been curtailed. However, Transmission Providers off the contract path are not obligated to reconfigure their transmission system or provide other congestion management procedures unless special arrangements are in place. Because the Interchange Transaction is considered firm “everywhere,” the Reliability Authority may attempt to arrange for Transmission Operators to reconfigure transmission or provide other congestion management options or Balancing Authorities to redispatch, even if they are off the contract path, to try to avoid curtailing the Interchange Transaction that is using the Firm Point-to-Point Transmission Service. 


5. Parallel Flow Calculation Procedure for Reallocating or Curtailing Firm Transmission Service

Introduction

The provision of Point-to-Point (PTP) transmission service, Network Integration (NI) transmission service and service to Native Load (NL) results in parallel flows on the transmission network of other Transmission Operators.  When a transmission facility becomes constrained curtailment of Interchange Transactions is required to allow Interchange Transactions of higher priority to be scheduled (Reallocation) or to provide transmission loading relief (Curtailment).  An Interchange Transaction is considered for Reallocation or Curtailment if its Transfer Distribution Factor (TDF) exceeds the TLR Curtailment Threshold. 

In compliance with the Pro Forma tariffs filed with FERC by Transmission Providers, Interchange Transactions using Non-firm PTP transmission service are curtailed first (TLR Level 3a and 3b), followed by transmission reconfiguration (TLR Level 4), and then the curtailment of Interchange Transactions using Firm PTP transmission service, NI transmission service and service to NL (TLR Level 5a and 5b). Curtailment of Firm PTP transmission service shall be accompanied by the comparable curtailment of NI transmission service and service to NL to the degree that these three transmission services contribute to the Constraint.

5.1. General Requirements
A methodology, called the Per Generator Method Without Counter Flow, or simply the Per Generator Method, has been programmed into the Interchange Distribution Calculator (IDC) to calculate the portion of parallel flows on any Constrained Facility due to service to NL of each Balancing Authority (BA).   The following general requirements are necessary to assure comparable Reallocation or Curtailment of firm transmission service:

5.1.1. The Reliability Authority initiating a curtailment shall identify for curtailment all firm transmission services (i.e. PTP, NI and service to NL) that contribute to the flow on any Constrained Facility by an amount greater than or equal to the Curtailment Threshold on a pro rata basis.

5.1.2. For Firm PTP transmission services, the Transfer Distribution Factors (TDFs) must be greater than or equal to the Curtailment Threshold before the transaction shall be considered for curtailment. 

5.1.3. For NI transmission service and service to NL, the generator-to-load distribution factors (GLDFs) must be greater than or equal to the Curtailment Threshold before the generation shall be considered for re-dispatch. The GLDF on a specific Constrained Facility for a given generator within a Balancing Autority is defined as the generator’s contribution to the flow on that flowgate when supplying the load of that Balancing Authority.

5.1.4. The Per Generator Method shall assign the amount of Constrained Facility relief that must be achieved by each Balancing Authority’s NI transmission service or service to NL.  It shall not specify how the reduction will be achieved.

5.1.5. All Balancing Authorities in the Eastern Interconnection shall be obligated to achieve the amount of Constrained Facility relief assigned to them by the Per Generator Method.

5.1.6. The implementation of the Per Generator Method shall be based on transmission and generation information that is readily available.

5.2. Calculation Method

The calculation of the flow on a Constrained Facility due to NI transmission service or service to NL shall be based on the Generation Shift Factors (GSFs) of a Balancing Authority’s assigned generation and the Load Shift Factors (LSFs) of its native load, relative to the system swing bus. The GSFs shall be calculated from a single bus location in the common reliability model used for each interconnection (i.e. the IDC model). The LSFs shall be defined as a general scaling of the native load within each Balancing Authority. The Generator to Load Distribution Factor (GLDF) shall be calculated as the GSF minus the LSF.  The common reliability model shall report all generators assigned to native load for which the GLDF is greater than or equal to the Curtailment Threshold.
6. Interchange Transaction Reallocation During TLR Levels 3a and 5a

Introduction

This standard provides the details for implementing TLR Levels 3a and 5a, both of which provide a means for reallocation of Transmission Service.

TLR Level 3a accomplishes Reallocation by curtailing Interchange Transactions using Non-firm Point-to-Point Transmission Service to allow Interchange Transactions using higher priority Non-firm or Firm Point-to-Point Transmission Service to start. (See Requirement 2.3, “TLR Level 3a.”) When a TLR Level 3a is in effect, Reliability Authorities shall reallocate interchange transactions according to the Transactions’ transmission service priorities. Reallocation also includes the orderly reloading of Transactions by priority when conditions permit curtailed Transactions to be reinstated.

TLR Level 5a accomplishes Reallocation by curtailing Interchange Transactions using Firm Point-to-Point Transmission Service on a pro-rata basis to allow new Interchange Transactions using Firm Point-to-Point Transmission Service to begin, also on a pro-rata basis. (See Requirement 2.6, “TLR Level 5a.”)
6.1. General Requirements

The basic requirements for Transaction Reallocation are built upon the premises of FERC Order 888, NERC Operating Policies and current business practices. Specifically, the key requirements are:

6.1.1. When identifying transactions for Reallocation the Reliability Authority shall normally only involve curtailments of Interchange Transactions using Non-firm Point-to-Point Transmission Service during TLR 3a. However, Reallocation may be used during TLR 5a to allow the implementation of additional Interchange Transactions using Firm Transmission Service on a pro-rata basis. 

6.1.2. When identifying transactions for Reallocation, the Reliability Authority shall only consider those Interchange Transactions at or above the Curtailment Threshold for which a TLR 2 or higher is called. 

6.1.3. When identifying transactions for Reallocation, the Reliability Authority shall displace Interchange Transactions utilizing lower priority transmission service with Interchange Transactions utilizing higher transmission service priority.
6.1.4. When identifying transactions for Reallocation, the Reliability Authority shall not curtail Interchange Transactions using Non-firm Transmission Service to allow the start or increase of another transaction having the same Non-Firm Transmission Service priority (marginal “bucket”).

6.1.5. When identifying transactions for Reallocation, the Reliability Authority shall reload curtailed Interchange Transactions prior to starting new or increasing existing Interchange Transactions. 

6.1.6. Interchange Transactions whose tags were submitted to the Tag Authority prior to the TLR 2 or 3a being called, but were subsequently held from starting because they failed to meet the Approved-Tag Submission Deadline for Reallocation (see Requirement 3, “Communications and Timing Requirements”), shall be considered to have been curtailed and thus would be eligible for reload at the same time as the curtailed Interchange Transaction.

6.1.7. The Reliability Authority shall reload or start all eligible Transactions on a pro-rata basis.

6.1.8. Interchange Transactions whose tags meet the Approved-Tag Submission Deadline for Reallocation (see Requirement 3, “Communications and Timing Requirements”) shall be considered for reallocation for the upcoming hour. (However, Interchange Transactions using Firm Point-to-Point Transmission Service shall be allowed to start as scheduled.) Interchange Transactions whose tags are submitted to the Interchange Distribution Calculator after the Approved-Tag Submission Deadline for Reallocation will be considered for Reallocation the following hour. This applies to Interchange Transactions using either Non-firm Point-to-Point Transmission Service or Firm Point-to-Point Transmission Service. If an Interchange Transaction using Firm Interchange Transaction is submitted after the Approved-Tag Submission Deadline and after the TLR is declared, that Transaction shall be held and then allowed to start in the upcoming hour.

It should be noted that calling a TLR 3a does not necessarily mean that Interchange Transactions using Non-firm Transmission Service will always be curtailed the next hour. However, TLR Levels 3a and 5a trigger the Approved-Tag Submission Deadline for Reallocation requirements and allow for a coordinated assessment of all Interchange Transactions tagged to start the upcoming hour.
6.2. Communication and Timing requirements

The following timeline shall be utilized to support Reallocation decisions during TLR Levels 3a or 5a. See Figures 2 and 3 for a depiction of the Reallocation Time Line.

6.2.1. [image: image1.wmf]00:00

01:00

00:20

00:10

00:30

00:40

00:50

00:25

Beginning of

Current Hour

Approved-Tag

Submission

Deadline for

Reallocation

(Must be in IDC for

Realloction at 01:00)

SC Sends Reallocation

notifications. CAs

curtail Non-firm

Transactions

and notify PSEs

TLR 3a

Firm Transactions

that are in IDC by

00:25 or by the

time the TLR is

declared (if later)

start as scheduled

TLR Re-issue

Alarm

Congestion

Management

Report to Issuing

Security Coordinator

Congestion Management

Report confirmed by Issuing

Security Coordinator

Congestion

Management

Report confirm by

Security Coordinator of

Sink Control Area

00:35

Adjust Lists sent to LCAs,

GCAs, authoring PSEs

00:45

Adjust

Tables from

LCAs

Potential Adjust List

Issued

Reallocation begins for Non-

firm Transactions that are in

IDC by 00:25 and for Firm

Transactions that are in by

the time the TLR is declared if

it is declared after 00:25.

Others are held for

Reallocation at 02:00.

[image: image2.wmf]Allocation based on Weighted Impact

1

2

3

4

5

6

7

8

9

Transaction 

ID

Initial 

Transaction

Distribution 

Factor

(1)*(2) 

Impact On 

Interface

(2)/(2TOT) 

Impact 

weighting 

factor

(3)*(4) 

Weighted 

Max Interface 

Reduction

(5)*(Relief 

Requested)

/(5 Tot) 

Interface 

Reduction

(6)/(2) 

Transaction 

Reduction

(1)-(7)     New 

Transaction 

Amount

(8)*(2) 

Adjusted 

Impact On 

Interface

Example 1

A-D(1)

800

0.6

480

0.34

164.57

209.73

349.54

450.46

270.27

A-D(2)

200

0.6

120

0.34

41.14

52.43

87.39

112.61

67.57

B-D

800

0.15

120

0.09

10.29

13.11

87.39

712.61

106.89

C-D

100

0.2

20

0.11

2.29

2.91

14.56

85.44

17.09

E-B

100

0.05

5

0.03

0.14

0.18

3.64

96.36

4.82

F-B

100

0.15

15

0.09

1.29

1.64

10.92

89.08

13.36

2100

1.75

760

219.71

280.00

553.45

1546.55

480.00

Example 2

A-D(1)

1000

0.6

600

0.52

313.04

262.16

436.93

563.07

337.84

B-D

800

0.15

120

0.13

15.65

13.11

87.39

712.61

106.89

C-D

100

0.2

20

0.17

3.48

2.91

14.56

85.44

17.09

E-B

100

0.05

5

0.04

0.22

0.18

3.64

96.36

4.82

F-B

100

0.15

15

0.13

1.96

1.64

10.92

89.08

13.36

2100

1.15

760

334.35

280.00

553.45

1546.55

480.00

Example 3

A-D(1A)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

A-D(1B)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

A-D(1C)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

A-D(1D)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

A-D(2)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

B-D

800

0.15

120

0.04

5.07

13.11

87.39

712.61

106.89

C-D

100

0.2

20

0.06

1.13

2.91

14.56

85.44

17.09

E-B

100

0.05

5

0.01

0.07

0.18

3.64

96.36

4.82

F-B

100

0.15

15

0.04

0.63

1.64

10.92

89.08

13.36

2100

3.55

760

 

108.31

280.00

553.45

1546.55

480.00

Time Convention. In this document, the beginning of the current hour shall be referenced as 00:00. The beginning of the next hour shall be referenced as 01:00. The end of the next hour shall be referenced as 02:00 (see Figure 1 at right).

6.2.2. Approved-Tag Submission Deadline for Reallocation. Reliability Authorities shall consider all approved Tags for Interchange Transactions at or above the Curtailment Threshold that have been submitted to the Interchange Distribution Calculator by 00:25 for Reallocation at 01:00. (See Figure 1 at the right). (However, Interchange Transactions using Firm Point-to-Point Transmission Service will be allowed to start as scheduled.)

6.2.2.1. Reliability Authorities shall consider all approved tags submitted to the Interchange Distribution Calculator beyond these deadlines (for both Firm and Non-firm Point-to-Point Transmission Service) for Reallocation at 02:00. 
6.2.2.2. The Approved-Tag Submission Deadline for Reallocation shall cease to be in effect as soon as the TLR level is reduced to 1 or 0.
Figure 2 - Reallocation timing for TLR 3a called at 00:08.


[image: image20.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

TLR 3b

IDC issues

Congestion

Management

Report based on

time of calling

TLR 3b. ADJUST

List follows.

Firm Transactions

that are in IDC by

00:25 may start as

scheduled

Firm Transactions

must be submitted

to IDC by 00:25 to

start as scheduled

TLR 2 or higher


6.2.3. Off-hour Transactions. Interchange Transactions with a Start Time other than xx:00 shall be considered for Reallocation at xx+1:00. For example, an Interchange Transaction with a start time of 01:05 and whose Tag was submitted at 00:15 will be considered for Reallocation at 02:00.

6.2.4. Tag Evaluation Period. Balancing Authorities and Transmission Providers shall evaluate all tags submit for reallocation and shall communicate approval or rejection (via the Tag Approval) by 00:25.

6.2.5. Collective Scheduling Assessment Period. At 00:25, the initiating Reliability Authority (the one who called and still has a TLR 3a or 5a in effect) shall run the IDC to obtain a three-part list of Interchange Transactions including their transaction status: 

6.2.5.1. Interchange Transactions that may start, increase, or reload shall have a status of PROCEED, 
6.2.5.2. Interchange Transactions that must be curtailed or Interchange Transactions whose tags were submitted prior to the TLR 2 or higher being declared but were not permitted to start or increase shall have a status of CURTAILED, and 

6.2.5.3. [image: image3.emf]00:00

Beginning of

Current Hour

01:00 02:00

Beginning of

Next Hour

00:25

Approved-Tag

Submission

Deadline for

Reallocation at 01:00

Approved-Tag

Submission

Deadline for

Reallocation at 02:00

01:25

Interchange Transactions that are entered into the IDC after 00:25 shall have a status of HOLD
 and be considered for Reallocation at 02:00. Also, Interchange Transactions using Non-firm Point-to-Point Transmission Service submitted to the Tag Authority after TLR 2 or higher was declared (“post-tagged”) but have not been allowed to start shall retain the HOLD status until given permission to PROCEED or E-Tag expires. (Note: TLR Level 2 does not hold Interchange Transactions using Firm Point-to-Point Transmission Service).
Figure 3 - Reallocation timing for TLR 5a called at 00:08.

6.2.5.4. The initiating Reliability Authority shall communicate the list to the appropriate sink Reliability Authorities via the IDC, who shall in turn communicate the list to the Sink Balancing Authorities at 00:30 for appropriate actions to implement Interchange Transactions (CURTAIL, PROCEED or HOLD). The IDC will prompt the initiating Reliability Authority to input the necessary information (i.e., maximum flowgate loading and curtailment requirement) into the IDC by 00:25. 
6.2.5.5. Subsequent required reports before 01:00 shall allow the Reliability Authorities to include those Interchange Transactions whose tags were submitted to the IDC after the Approved-Tag Submission Time for Reallocation and were given the HOLD status (not permitted to PROCEED). Transactions at or above the Curtailment Threshold that are not indicated as “PROCEED” on Reload/Reallocation Report shall not be permitted to start or increase the next hour.

Note that TLR 2 does not initiate the Approved-Tag Submission Deadline for Reallocation, but a TLR3a or 5a does. It is, however, important to recognize the time when a TLR 2 is called, where applicable, to determine the status of a held transaction – “CURTAILED” if tagged before the TLR was called but “HOLD” if tagged after the TLR was called.

6.2.5.6. In running the IDC, the Reliability Authority shall have an option to specify the maximum loading of the Constrained Facility by all Interchange Transactions using Point-to-Point Transmission Service. This allows the Reliability Authority to take into consideration SYSTEM OPERATING LIMITs or INTERCONNECTION RELIABILITY OPERATING LIMITs and changes in Transactions using other than point-to-point service taken under the OATT. This option is needed to avoid loading the Constrained Facility to its limit with known Interchange Transactions while other factors push the facility into a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT violation and hence triggering the declaration of a TLR 3b or 5b.

6.2.5.7. Notification of Interchange Transaction status shall be provided  from the IDC to the Reliability Authorities via an IDC Report. The Reliability Authorities shall communicate this information to the Balancing Authorities and Transmission Operators. 

Additional reporting and communications details on information posted from the IDC to the NERC TLR site are contained in Attachment E.

6.2.6. Customer Preferences on Timing to Call TLR 3a or 5a. Reliability Authorities should leave a TLR 2 and call a TLR 3a as soon as possible (but no later than 30 minutes) to initiate the Approved-Tag Submission Deadline and start reallocating Transactions. Nevertheless, recognizing the Approved-Tag Submission Deadline for Reallocation for Reallocation, from a Transmission Customer perspective, it is preferable that the Reliability Authority call TLR 3a within a certain time period to allow for tag preparation and submission.  See Figure 4.

For example, a TLR 3a initiated during the period 01:00 to 01:25 would allow the Purchasing-Selling Entity to submit a Tag for entry into the Interchange Distribution Calculator by the Approved-Tag Submission Deadline for reallocation at 02:00 (see Figure 4 at right).  However, the preferred time period to declare a TLR 3a or 5a would be 00:40 (when tags for Next Hour Market have been submitted) and 01:15. This will allow the Transmission Customers a range of 15 to 35 minutes to prepare and submit tags. (Note: In this situation, the Reliability Authority would need to reissue the TLR 3a at 01:00.)

It must be emphasized that the preferred time period is not a requirement, and should not in any way impede a Reliability Authority’s ability to declare a TLR 3a, 3b, 4, 5a, or 5b whenever the need arises.

Figure 4. “Ideal" time for issuing TLR 3a for Reallocation at 02:00.

[image: image4.emf]00:00 01:00

01:25

Approved-Tag

Submission

Deadline for

Reallocation

Period

for initiating TLR 3A

for Reallocation at start

of next  hour

02:00

00:40



7. Interchange Transaction Curtailments During TLR Level 3b

Introduction

This standard provides the details for implementing TLR Level 3b, which curtails Interchange Transactions using Non-firm Point-to-Point Transmission Service to assist the Reliability Authority to recover from SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT violations.

TLR Level 3b curtails Interchange Transactions using Non-firm Point-to-Point Transmission Service that are at or above the Curtailment Threshold. (See Requirement 2.4, “TLR Level 3b.”). Furthermore, all new Interchange Transactions using Non-firm Point-to-Point Transmission Service that are at or above the Curtailment Threshold during the TLR 3b implementation period are halted or held. Transactions using Firm Point-to-Point Transmission Service will be allowed to start if they are submitted to the IDC within specific time limits as explained in Appendix F, “Considerations for Interchange Transactions using Firm Point-to-Point Transmission Service.” Those Interchange Transactions using Firm Point-to-Point Transmission Service that are not submitted to the IDC within these time limits will be held. 

Basic Requirements
7.1. The Reliability Authority shall be allowed to call a TLR 3b at any time to help mitigate a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT violation.

7.2. The Reliability Authority shall only consider those Interchange Transactions at or above the Curtailment Threshold for curtailment, holding, or halting.

7.3. The Reliability Authority shall curtail existing Interchange Transactions using Non-firm Point-to-Point Transmission Service as necessary to provide the required relief on the Constrained Facility.

7.4. The Reliability Authority shall curtail additional Interchange Transactions using Non-firm Point-to-Point Transmission Service to provide room for Interchange Transactions using Firm Point-to-Point Transmission Service if those Interchange Transactions using Firm Point-to-Point Transmission Service are scheduled to start during the current hour or the following hour.
7.5. The Reliability Authority shall not allow existing Interchange Transactions using Non-firm Point-to-Point Transmission Service that are not curtailed to increase (they may flow at the same or reduced level).

7.6. The Reliability Authority shall not Reallocate Interchange Transactions using Non-firm Point-to-Point Transmission Service during a TLR 3b.

7.7. The Reliability Authority shall allow Interchange Transactions using Firm Point-to-Point Transmission Service to start as explained in Appendix F, “Considerations for Interchange Transactions using Firm Point-to-Point Transmission Service.”

7.8. The Reliability Authority shall progress to TLR Level 5b as necessary if there is still insufficient room for Interchange Transactions using Firm Point-to-Point Transmission Service to start as scheduled after all Interchange Transactions using Non-firm Point-to-Point Transmission Service have been curtailed. ,.

7.9. The common interconnect model utilized by the Reliability Authorities (i.e. the IDC) will issue ADJUST Lists to the Generation and Load Control Areas and the Purchasing-Selling Entity who submitted the tag. The ADJUST List will include:

7.9.1. Interchange Transactions using Non-firm Point-to-Point Transmission Service that are to be curtailed, halted, or held during Current and Next hours.

7.9.2. Interchange Transactions using Firm Point-to-Point Transmission Service that were entered after 00:25 or issuance of TLR 3b (see Case 3 in Appendix F).
7.10. The Load Balancing Authority shall send the ADJUST Tables back to the IDC as soon as possible to ensure the most accurate calculations for actions subsequent to the TLR 3b being called.

7.11. The Reliability Authority shall be allowed to call a TLR Level 3a as soon as the SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT Violation has been mitigated.

7.11.1. If the TLR Level 3a is called before the hour 01, then a Reallocation shall be computed for the start of that hour.

7.11.2. Transactions must be in the IDC by the Approved-tag Submission Deadline for Reallocation (see Requirement 2).

Appendices for NAESB Transmission Loading Relief Standard

Appendix A. Transaction Management and Curtailment Process

Appendix B. Transaction Curtailment Formula
Appendix C. Sample NERC Transmission Loading Relief Procedure Log
Appendix D. Examples for Parallel Flow Calculation Procedure for Reallocating or Curtailing Firm Transmission Service
Appendix E. How the IDC Handles Reallocation

Appendix F. Considerations for Interchange Transactions using Firm Point-to-Point Transmission Service

Appendix A. Transaction Management and Curtailment Process

[image: image5.wmf]00:00

01:00

Beginning of

Next Hour

00:20

00:10

00:30

00:40

00:50

00:25

Beginning of

Current Hour

Approved-Tag

Submission

Deadline for

Reallocation

(Must be in IDC for

Realloction at 01:00)

SC Sends Reallocation

notifications. CAs

implement reductions of Firm

Transactions on pro-rata basis

and notify PSEs

Firm Transactions

that are in IDC by

time TLR is

declared or 00:25,

whichever is later,

start as scheduled

TLR 5a

Reallocation begins for Firm

Transactions that are in IDC

by time TLR is declared or

00:25, whichever is later.

Others are held for

Reallocation at 02:00

This flowchart depicts an overview of the Transaction Management and Curtailment process. Detailed decisions are not shown.

Appendix B Transaction Curtailment Formula

Example

This example is based on the premise that a transaction should be curtailed in proportion to its TDF on the Constraints. Its effect on the interface is a combination of its size in MW and its effect based on its distribution factor.

	Column
	Description

	1.
Initial Transaction
	Interchange Transaction before the TLR Procedure is implemented.

	2.
Distribution Factor
	Proportional effect of the Transaction over the constrained interface due to the physical arrangement and impedance of the transmission system.

	3.
Impact on the Interface
	Result of multiplying the Transaction MW by the distribution factor. This yields the MW that flow through the constrained interface from the Transaction. Performing this calculation for each Transaction yields the total flow through the constrained interface from all the Interchange Transactions. In this case, 760 MW.

	4.
Impact Weighting Factor
	“Normalization” of the total of the Distribution Factors in Column 2. Calculated by dividing the Distribution Factor for each Transaction by the total of the Distribution Factors.

	5.
Weighted Maximum Interface Reduction
	Multiplying the Impact on the Interface from each Transaction by its Impact Weighting Factor yields a new proportion that is a combination of the MW Impact on the Interface and the Distribution Factor.

	6.
Interface Reduction
	Multiplying the amount we need to reduce the flow over the constrained interface (280 MW) by the normalization of the Weighted Maximum Interface Reduction yields the actual MW reduction that each Transaction must contribute to achieve the total reduction.

	7.
Transaction Reduction
	Now we have to divide by the Distribution Factor to see how much the Transaction must be reduced to yield the result we calculated in Column 7. Note that the reductions for the first two Interchange Transactions (A-D (1) and A-D (2) are in proportion to their size since their distribution factors are equal.

	8.
New Transaction Amount
	Subtracting the Transaction Reduction from the Initial Transaction yields the New Transaction Amount.

	9.
Adjusted Impact on Interface
	A check to ensure the new constrained interface MW flow has been reduced to the target amount.


[image: image6.wmf]Allocation based on Weighted Impact

1

2

3

4

5

6

7

8

9

Transaction 

ID

Initial 

Transaction

Distribution 

Factor

(1)*(2) 

Impact On 

Interface

(2)/(2TOT) 

Impact 

weighting 

factor

(3)*(4) 

Weighted 

Max Interface 

Reduction

(5)*(Relief 

Requested)

/(5 Tot) 

Interface 

Reduction

(6)/(2) 

Transaction 

Reduction

(1)-(7)     New 

Transaction 

Amount

(8)*(2) 

Adjusted 

Impact On 

Interface

Example 1

A-D(1)

800

0.6

480

0.34

164.57

209.73

349.54

450.46

270.27

A-D(2)

200

0.6

120

0.34

41.14

52.43

87.39

112.61

67.57

B-D

800

0.15

120

0.09

10.29

13.11

87.39

712.61

106.89

C-D

100

0.2

20

0.11

2.29

2.91

14.56

85.44

17.09

E-B

100

0.05

5

0.03

0.14

0.18

3.64

96.36

4.82

F-B

100

0.15

15

0.09

1.29

1.64

10.92

89.08

13.36

2100

1.75

760

219.71

280.00

553.45

1546.55

480.00

Example 2

A-D(1)

1000

0.6

600

0.52

313.04

262.16

436.93

563.07

337.84

B-D

800

0.15

120

0.13

15.65

13.11

87.39

712.61

106.89

C-D

100

0.2

20

0.17

3.48

2.91

14.56

85.44

17.09

E-B

100

0.05

5

0.04

0.22

0.18

3.64

96.36

4.82

F-B

100

0.15

15

0.13

1.96

1.64

10.92

89.08

13.36

2100

1.15

760

334.35

280.00

553.45

1546.55

480.00

Example 3

A-D(1A)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

A-D(1B)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

A-D(1C)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

A-D(1D)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

A-D(2)

200

0.6

120

0.17

20.28

52.43

87.39

112.61

67.57

B-D

800

0.15

120

0.04

5.07

13.11

87.39

712.61

106.89

C-D

100

0.2

20

0.06

1.13

2.91

14.56

85.44

17.09

E-B

100

0.05

5

0.01

0.07

0.18

3.64

96.36

4.82

F-B

100

0.15

15

0.04

0.63

1.64

10.92

89.08

13.36

2100

3.55

760

 

108.31

280.00

553.45

1546.55

480.00

[image: image7.wmf]A

800

 (450)

200 

(112)

D

B

800 

(713)

C

100

 (85)

E

100 

(96)

F

100 

(89)


[image: image8.wmf]System

Secure

OSL Violation

Monitor

System

Security Limit

Violation?

Potential

SLV?

TLR 1

Request

for Transmission

Service?

Accommodate?

TLR 2 

Hold

Request for Higher Priority

Service

TLR 3a 

Curtail Non-firm

Accommodate?

TLR 4 

Reconfigure

Accommodate?

TLR 5a 

TCF 

Curtail Firm

TLR 3b

Curtailment

Method:

Local

Still

Constrained?

NERC TLR

IDC

Curtail Non-Firm 

Priorities 1-6

Still

Constrained?

Can

Reconfigure?

TLR 4 

Reconfigure

TLR 5b 

Calc TCF 

Curtail Firm

Still

Constrained?

Take

Emergency

Action

No

Yes

Yes

No

No

Yes

Yes

No

Yes

No

Yes

No

No

Yes

No

Yes

Yes

No

No

Yes

Appendix C. Sample NERC Transmission Loading Relief Procedure Log

Appendix D. Examples for Parallel Flow Calculation Procedure for Reallocating or Curtailing Firm Transmission Service

The NERC “Parallel Flow Calculation Procedure Reference Document” provides additional information about the criteria used to include generators in the IDC calculation process.

Example of Results of Calculation Method

An example of the output of the IDC calculation of curtailment of firm transmission service is provided below for the specific Constrained Facility identified in the Book of Flowgates as Flowgate 1368.  In this example, a total Firm PTP contribution to the Constrained Facility, as calculated by the IDC, is assumed to be 21.8 MW. 

The table below presents a summary of each Balancing Authority’s responsibility to provide relief to the Constrained Facility due to its NI transmission service and service to NL contribution to the Constrained Facility.  In this example, Balancing Authority LAGN would be requested to curtail 17.3 MW of its total of 401.1 MW of flow contribution on the Constrained Facility. See the “Parallel Flow Calculation Procedure Reference Document” for additional details regarding the information illustrated in the table (e. g. Scaled P Max and Flowgate NNL MW).

In summary, Interchange transactions would be curtailed by a total of 21.8 MW and NI transmission service and service to NL would be curtailed by a total of 178.2 MW by the five Balancing Authorities identified in the table.  These curtailments would provide a total of 200.0 MW of relief to the Constrained Facility.

	Sink RA

	Service Point

	Scaled
P Max

	Flowgate
NNL MW

	Current NNL Relief

	NNL Responsibility

	NNL Responsibility

Acknowledgement


						Inc/Dec

	Current Hr

	Acknowledge

Time

	Total MW

Resp.


	EES

	EES

	8429.7

	2991.4

	0.0

	128.9

	128.9

	13:44

	128.9


	EES

	LAGN

	1514.0

	718.6

	0.0

	31.0

	31.0

	13:44

	31.0


	SOCO

	SOCO

	5089.2

	401.1

	0.0

	17.3

	17.3

	13:44

	17.3


	SWPP

	CLEC

	235.7

	18.0

	0.0

	0.8

	0.8

	13:42

	0.8


	SWPP

	LEPA

	22.8

	4.1

	0.0

	0.2

	0.2

	13:42

	0.2


	Total

	15291.4
	4133.2
	0.0

	178.2
	178.2
		178.2


	


Appendix E. How the IDC Handles Reallocation

The Interchange Distribution Calculator algorithms reflect the reallocation and reloading principles in this Appendix, as well as the reporting requirements, and status display. The IDC will obtain the Tag Submittal Time from the Tag Authority, and post the Reloading/ Reallocation information to the NERC TLR site. 

A summary of IDC features that support the reallocation process is provided in Attachment E1. Details on the interface and display features are provided in Attachment E2.
Attachment E1 – Summary of IDC Features that Support Transaction Reloading/Reallocation 

The following is a summary of IDC features and E-Tag interface that support Reloading/Reallocation: 

Information posted from IDC to NERC TLR site.

1. Restricted directions (all source/sink combinations that impact a Constrained Facility(ies) with TLR 2 or higher) will be posted to the NERC TLR site and updated as necessary. 

2. TLR Constrained Facility status and Transfer Distribution Factors will continue to be posted to NERC TLR site. 

3. Lowest priority of Interchange Transactions (marginal “bucket”) to be Reloaded/Reallocated next-hour on each TLR Constrained Facility will be posted on NERC TLR site. This will provide an indication to the market of priority of Interchange Transactions that may be Reloaded/Reallocated the following hours. 

IDC Logic, IDC Report, and Timing

1. The Reliability Authority will run the IDC the Reloading/Reallocation report at approximately 00:26 The IDC will prompt the Reliability Authority to enter a maximum loading value. The IDC will alarm if the Reliability Authority doesn’t enter this value and issue a report by 00:30 or change from TLR 3a Level. The Report will be distributed to Balancing Authorities and Transmission Operators at 00:30. This process repeats every hour as long as the Approved-Tag Submission Deadline for Reallocation is in effect (or until the TLR level is reduced to 1 or 0).

2. For Interchange Transactions in the restricted directions, tags must be submitted to the Interchange Distribution Calculator by the Approved-Tag Submission Deadline for Reallocation to be considered for Reallocation next-hour. The time stamp by the Tag Authority is regarded the official tag submission time.

3. Tags submitted to Interchange Distribution Calculator after the Approved-Tag Submission Deadline for Reallocation will not be allowed to start or increase but will be considered for Reallocation the next hour. 

4. Interchange Transactions in restricted directions that are not indicated as “PROCEED” on the Reload/Reallocation Report will not be permitted to start or increase next hour.

Reloading/Reallocation Transaction Status

Reloading/Reallocation status will be determined by the IDC for all Interchange Transactions. The Reloading/Reallocation status of each Interchange Transaction will be listed on IDC reports and NERC TLR site as appropriate. An Interchange Transaction is considered to be in a restricted direction if it is at or above the Curtailment Threshold. Interchange Transactions below the Curtailment Threshold are unrestricted and free to flow subject to all applicable Policy and tariff rules. 

1. HOLD. Permission has not been given for Interchange Transaction to start or increase and is waiting for the next Reloading/Reallocation evaluation for which it is a candidate. Interchange Transactions with E-tags submitted to the Tag Authority prior to TLR 2 or higher being declared (pre-tagged) will change to CURTAILED Status upon evaluation that does not permit them to start or increase. Transactions with E-tags submitted to Tag Authority after TLR 2 or higher was declared (post-tagged) will retain HOLD Status until given permission to proceed or E-Tag expires.

2. CURTAILED. Transactions for which E-Tags were submitted to Tag Authority prior to TLR 2 or higher being declared (pre-tagged) and ordered to be curtailed totally, curtailed partially, not permitted to start, or not permitted to increase. Interchange Transactions (pre-tagged or post-tagged) that were flowing and ordered to be reduced or totally curtailed. The Balancing Authority   will indicate to the IDC through the E-Tag adjustment table the Interchange Transaction’s curtailed values.

3. PROCEED: Interchange Transaction is flowing or has been permitted to flow as a result of Reloading/Reallocation evaluation. The Balancing Authority  will indicate through the E-Tag adjustment table to IDC if Interchange Transaction will reload, start, or increase next-hour per PSE’s energy schedule as appropriate.

Reallocation/Reloading Priorities 

1. Interchange Transaction candidates are ranked for loading and curtailment by priority as per Appendix 9C1, Section E, “Principles for Mitigating Constraints On and Off the Contract Path”]. This is called the “Constrained Path Method,” or CPM. (secondary, hourly, daily, … firm etc). Interchange Transactions are curtailed and loaded pro-rata within priority level per TLR algorithm.

2. Reloading/Reallocation of Interchange Transactions are prioritized first by priority per CPM. E-Tags must be submitted to the Interchange Distribution Calculator by the Approved-Tag Submission Deadline for Reallocation of the hour during which the Interchange Transaction is scheduled to start or increase to be considered for Reallocation. 

3. During Reloading/Reallocation, Interchange Transactions using lower priority Transmission Service will be curtailed pro-rata to allow higher priority transactions to reload, increase, or start. Equal priority Interchange Transactions will not reload, start, or increase by pro-rata curtailment of other equal priority Interchange Transactions. 

4. Reloading of Interchange Transactions using Non-firm Transmission Service with CURTAILED Status will take precedence over starting or increasing of Interchange Transactions using Non-firm Transmission Service of the same priority with PENDING Statuses. 

5. INTERCHANGE TRANSACTIONS using Firm Point-to-Point Transmission Service will be allowed to start as scheduled under TLR 3a as long as their E-Tag was received by the Interchange Distribution Calculator by the Approved-Tag Submission Deadline for Reallocation of the hour during which the Interchange Transaction is due to start or increase, regardless of whether the E-tag was submitted to the Tag Authority prior to TLR 2 or higher being declared or not. If this is the initial issuance of the TLR 3a, Interchange Transactions using Firm Point-to-Point Transmission Service will be allowed to start as scheduled as long as their E-Tag was received by the Interchange Distribution Calculator by the time the TLR is declared.
Total Flow Value on a Constrained Facility for Next Hour 

1. The Reliability Authority will calculate the change in net flow on a Constrained Facility due to Reallocation for the next hour based on:

· Present constrained facility loading, present level of Interchange Transactions, and Balancing Authorities  NNL responsibility
 (TLR Level 5a) impacting the Constrained Facility,

· SYSTEM OPERATING LIMITs or INTERCONNECTION RELIABILITY OPERATING LIMITs , known interchange impacts and Balancing Authority NNL responsibility (TLR Level 5a) on the Constrained Facility the next hour, and

· Interchange Transactions scheduled to begin the next hour.

2. The Reliability Authority will enter a maximum loading value for the constrained facility into the IDC as part of issuing the Reloading/Reallocation report.

3. The Reliability Authority is allowed to call for TLR 3a or 5a when approaching a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT  to allow maximum transactional flow next hour, and to manage flows without violating transmission limits.

4. The simultaneous curtailment and Reallocation for a Constrained Facility is allowed. This reduces the flow over the Constrained Facility while allowing Interchange Transactions using higher priority Transmission Service to start or increase the next hour. This may be used to accommodate change in flow next-hour due to changes other than point-to-point Interchange Transactions while respecting the priorities of Interchange Transactions flowing and scheduled to flow the next hour. The intent is to reduce the need for using TLR 3b, which prevents new Interchange Transactions from starting or increasing the next hour. 

5. The Reliability Authority must allow Interchange Transactions to be reloaded as soon as possible. Reloading must be in an orderly fashion to prevent a SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT  violation from (re)occurring and requiring holding or curtailments in the restricted direction.

Attachment E2 – Timing Requirements

TLR Levels 3a and 5a Issuing/Processing Time Requirement

1. [image: image9.wmf]SAVE FILE DIRECTORY:

NERC TRANSMISSION LOADING RELIEF (TLR) PROCEDURE LOG 

FILE SAVED AS:

  .XLS

INCIDENT :

  

DATE:

 

IMPACTED SECURITY COORDINATOR   :

 

ID NO:

 

I N I T I A L      C O N D I T I O N S

Limiting Flowgate  (LIMIT)

Rating

Contingent Flowgate  (CONT.)

ODF 

 

 

TLR Levels

Priorities

NX

Next Hour Market Service

0: TLR Incident Canceled

NS

Service over secondary receipt and delivery points

1. Notify Security Coordinators of potential problems.

NH

Hourly Service

2: Halt additional transactions that contribute to the overload

ND

Daily Service

3a and 3b: Curtail transactions using Non-firm Transmission Service

NW

Weekly Service

4. Reconfigure to continue firm transactions if needed.

NM

Monthly Service

5a and 5b: Curtail Transactions using Firm Transmission Service.

NN

Non-firm imports for native load and network customers from 

6: Implement emergency procedures.

non-designated network resources

F

Firm Service

T  L  R        A  C  T  I  O  N  S

TLR 3,5

TLR 3,5

LEVEL

TIME

Priority

No. TX

MW

Cont. Elem't

C O M M E N T S   A B O U T   A C T I O N S

Curtail

Curtail

Present

Post Cont.

Present

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

 

MW Flow

Limiting Element

In order for the IDC to be reasonably certain that a TLR Level 3a or 5a re-allocation/reloading report in which all tags submitted by the Approved-Tag Submission Deadline for Reallocation are included, the report must be generated no earlier than 00:25 to allow the 10-minute approval time for Transactions that start next hour. 

2. [image: image10.wmf]MW

Time

10

20

40

S1

TLR

In order to allow a Reliability Authority to declare a TLR Level 3a or 5a any time during the hour, the TLR declaration and Reallocation/Reloading report distribution will be treated as independent processes by IDC. That is, a Reliability Authority may declare a TLR Level 3a or 5a at any time during the course of an hour. However, if a TLR Level 3a or 5a is declared for the next hour prior to 00:25 (see Figure 5 at right), the Reallocation/Reloading report that is generated will be made available to the issuing Reliability Authority only for previewing purposes, and can not be distributed to the other Reliability Authorities or the market. Instead, the issuing Reliability Authority will be reminded by an IDC alarm at 00:25 to generate a new Reallocation/Reloading report that will include all tags submitted prior to the Approved-Tag Submission Deadline for Reallocation. 

3. A TLR Level 3a or 5a Reallocation/Reloading report must be confirmed by he issuing Reliability Authority prior to 00:30 in order to provide a minimum of 30 minutes for the Reliability Authorities with tags sinking in his Reliability Area to coordinate the Reallocation and Reloading with the Sink Balancing Authorities. This provides only 5 minutes (from 00:25 to 00:30) for the issuing Reliability Authority to generate a Reallocation/Reloading report, review it, and approve it.

4. The TLR declaration time will be recorded in the IDC for evaluating transaction sub-priorities for Reallocation/Reloading purposes (see Subpriority Table, Page RAL-13).

Re-Issuing of a TLR Level 2 or Higher

Each hour, the IDC will automatically remind the issuing Reliability Authority (via an IDC alarm) of a TLR level 2 or higher declared in the previous hour or earlier about re-issuing the TLR. The purpose of the reminder is to enable the Reliability Authority to Reallocate or reload currently halted or curtailed Interchange Transactions next hour. The reminder will be in the form of an alarm to the issuing Reliability Authority, and will take place at 00:25 so that, if the Reliability Authority re-issues the TLR as a TLR level 3a or 5a, all tags submitted prior to the Approved-Tag Submission Deadline for Reallocation are available in the IDC. 

IDC Assistance with Next Hour PTP Transactions

In order to assist a Reliability Authority in determining the MW relief required on a Constrained Facility for the next hour for a TLR level 3a or 5a, the IDC will calculate and present the total MW impact of all currently flowing and scheduled Point-to-Point Transactions for the next hour. In order to assist a Reliability Authority in determining the MW relief required on a Constrained Facility for the next hour during a TLR level 5a, the IDC will calculate and present the total MW impact of all currently flowing and scheduled Point-to-Point Transactions for the next hour as well as Balancing Authority with flows due to service to Network Customers and Native Load. The Reliability Authority will then be requested to provide the total incremental or decremental MW amount of flow through the Constrained Facility that can be allowed for the next hour. The value entered by the Reliability Authority and the IDC-calculated amounts will be used by the IDC to identify the relief/reloading amounts (delta incremental flow value) on the constrained facility. The IDC will determine the Transactions to be reloaded, reallocated, or curtailed to make room for the Transactions using higher priority Transmission Service. The following examples show the calculation performed by IDC to identify the “delta incremental flow”:

Example 1

	Flow to maintain on Facility
	800 MW

	Expected flow next hour from Transactions using Point-to-Point Transmission Service
	950 MW

	Contribution from flow next hour from service to Network customers and Native Load
	-100 MW

	Expected Net flow next hour on Facility
	850 MW

	Amount of Transactions using Point-to-Point Transmission Service to hold for Reallocation
	850 MW – 800 MW = 50 MW

	Amount to enter into IDC for Transactions using Point-to-Point Transmission Service
	950 MW – 50 MW = 900 MW


Example 2

	Flow to maintain on Facility
	800 MW

	Expected flow next hour from Transactions using Point-to-Point Transmission Service
	950 MW

	Contribution from flow next hour from service to Network customers and Native Load
	50 MW

	Expected Net flow next hour on Facility
	1000 MW

	Amount of Transactions using Point-to-Point Transmission Service to hold for Reallocation
	1000 MW – 800 MW = 200 MW

	Amount to enter into IDC for Transactions using Point-to-Point Transmission Service
	950 MW – 200 MW = 750 MW


Example 3

	Flow to maintain on Facility
	800 MW

	Expected flow next hour from Transactions using Point-to-Point Transmission Service
	950 MW

	Contribution from flow next hour from service to Network customers and Native Load
	-200 MW

	Expected Net flow next hour on Facility
	750 MW

	Amount of Transactions using Point-to-Point Transmission Service to hold for Reallocation
	750 MW – 800 MW = -50 MW

None are held


For a TLR levels 3b or 5b the IDC will request the Reliability Authority to provide the MW requested relief amount on the Constrained Facility, and will not present the current and next hour MW impact of PTP transactions. The RA-entered requested relief amount will be used by IDC to determine the Interchange Transaction Curtailments and flows due to service to Network Customers and Native Load (TLR Level 5b) in order to reduce the SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT  violation on the Constrained Facility by the requested amount. 

IDC Calculations and Reporting Requirements

At the time the TLR report is processed, the IDC will use all candidate Interchange Transactions for Reallocation that met the Approved-Tag Submission Deadline for Reallocation plus those Interchange Transactions that were curtailed or halted on the previous TLR action of the same TLR event. The IDC will calculate and present an Interchange Transactions Halt/Curtailment list that will include reload and Reallocation of Interchange Transactions. The Interchange Transactions are prioritized as follows:

1. All Interchange Transactions will be arranged by Transmission Service priority according to the Constrained Path Method. These priorities range from 1 to 6 for the various non-firm Transmission Service products (TLR levels 3a and 3b). Interchange Transactions using Firm Transmission Service (priority 7) are used only in TLR levels 5a and 5b. Next-Hour Market Service is included at priority 0 (zero) 

2. In a TLR Level 3a the Interchange Transactions using Non-firm Transmission Service in a given priority will be further divided into four sub-priorities, based on current schedule, current active schedule (identified by the submittal of a tag ADJUST message), next-hour schedule, and tag status. Solely for the purpose of identifying which Interchange Transactions to be loaded under a TLR 3a, various MW levels of an Interchange Transaction may be in different sub-priorities. The sub-priorities are as follows:

	Priority
	Purpose
	Explanation and Conditions

	S1
	To allow a flowing Interchange Transaction to maintain or reduce its current MW amount in accordance with its energy profile.
	The MW amount is the lowest between currently flowing MW amount and the next-hour schedule. The currently flowing MW amount is determined by the e-tag ENERGY PROFILE and ADJUST tables. If the calculated amount is negative, zero is used instead.

	S2
	To allow a flowing Interchange Transaction that has been curtailed or halted by TLR to reload to the lesser of its current-hour MW amount or next-hour schedule in accordance with its energy profile. 
	The Interchange Transaction MW amount used is determined through the e-tag ENERGY PROFILE and ADJUST tables. If the calculated amount is negative, zero is used instead.

	S3
	To allow a flowing Transaction to increase from its current-hour schedule to its next-hour schedule in accordance with its energy profile. 
	The MW amounts used in this sub-priority is determined by the e-tag ENERGY PROFILE table. If the calculated amount is negative, zero is used instead.

	S4
	To allow a Transaction that had never started and was submitted to the Tag Authority after the TLR (level 2 or higher) has been declared to begin flowing (i.e., the Interchange Transaction never had an active MW and was submitted to the IDC after the first TLR Action of the TLR Event had been declared.) 
	The Transaction would not be allowed to start until all other Interchange Transactions submitted prior to the TLR with the same priority have been (re)loaded. The MW amount used is the sub-priority is the next-hour schedule determined by the e-tag ENERGY PROFILE table.


Examples of Interchange Transactions using Non-firm Transmission Service sub-priority settings begin on page 16.

3. All Interchange Transactions using Firm Transmission Service will be put in the same priority group, and will be Curtailed/Reallocated pro-rata, independent of their current status (curtailed or halted) or time of submittal with respect to TLR issuance (TLR level 5a). Under a TLR 5a, all Interchange Transactions using Non-firm Transmission Service that is at or above the Curtailment Threshold will have been curtailed and hence sub-prioritizing is not required.

All Interchange Transactions processed in a TLR are assigned one of the following statuses:

PROCEED:
The Interchange Transaction has started or is allowed to start to the next hour MW schedule amount.

CURTAILED:
The Interchange Transaction has started and is curtailed due to the TLR, or it had not started but it was submitted prior to the TLR being declared (level 2 or higher).

HOLD:
The Interchange Transaction had never started and it was submitted after the TLR being declared – the Interchange Transaction is held from starting next hour or the transaction had never started and it was submitted to the Interchange Distribution Calculator after the Approved-Tag Submission Deadline – the Interchange Transaction is to be held from starting next hour and is not included in the Reallocation calculations until following hour.

Upon acceptance of the TLR Transaction reallocation/reloading report by the issuing Reliability Authority, the IDC will generate a report to be sent to NERC that will include the PSE name and Tag ID of each Interchange Transaction in the IDC TLR report. The Interchange Transaction will be ranked according to its assigned status of HOLD, CURTAILED or PROCEED. The reloading/reallocation report will be made available at NERC’s public TLR site, and it is NERC’s responsibility to format and publish the report. 

Tag Reloading for TLR Levels 1 and 0

When a TLR Level 1 or 0 is issued, the Constrained Facility is no longer under SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT Violation and all Interchange Transactions are allowed to flow. In order to provide the Reliability Authorities with a view of the Interchange Transactions that were halted or curtailed on previous TLR actions (level 2 or higher) and are now available for reloading, the IDC provides such information in the TLR report. 

New Tag Alarming

Those Interchange Transactions that are at or above the Curtailment Threshold and are not candidates for reallocation because the tags for those Transactions were not submitted by the Approved-Tag Submission Deadline for Reallocation will be flagged as HOLD and must not be permitted to start or increase during the next hour. To alert Reliability Authorities of those Transactions required to be held, the IDC will generate a report (for viewing within the IDC only) at various times. The report will include a list of all HOLD Transactions. In order not to overwhelm the Reliability Authority with alarms, only those who issued the TLR and those whose Transactions sink within their Reliability Area will be alarmed. An alarm will be issued for a given tag only once and will be issued for all TLR levels for which halting new Transactions is required: TLR Level 2, 3a, 3b, 5a and 5b.

Tag Adjustment

The Interchange Transactions with statuses of HOLD, CURTAILED or PROCEED must be adjusted by a Tag Authority or Tag Approval entity. Without the tag adjustments, the IDC will assume that Interchange Transactions were not curtailed/held and are flowing at their specified schedule amounts. 

1. Interchange Transactions marked as CURTAILED should be adjusted to a cap equal to, or at the request of the originating PSE, less than the reallocated amount (shown as the MW CAP on the IDC report). This amount may be zero if the Transaction is fully curtailed.

2. Interchange Transaction marked as PROCEED should be adjusted to reload (NULL or to its MW level in accordance with its Energy Profile in the adjusted MW in the E-Tag) if the Interchange Transaction has been previously adjusted; otherwise, if the Interchange Transaction is flowing in full, the Tag Authority need not issue an adjust.

3. Interchange Transactions marked as HOLD should be adjusted to 0 MW.

Special Tag Status

There are cases in which a tag may be marked with a composite state of ATTN_REQD to indicate that tag Authority/Approval failed to communicate or there is an inconsistency between the validation software of different tag Authority/Approval entities. In this situation, the tag is no longer subject to passive approval and its status change to IMPLEMENT may take longer than 10 minutes. Under these circumstances, the IDC may have a tag that is issued prior to the Tag Submittal Deadline that will not be a candidate for reallocation. Such tags, when approved by the Tag Authority, will be marked as HOLD and must be halted. 

Transaction Sub-Priority Examples

The following describes examples of Interchange Transactions using Non-firm Transmission Service sub-priority setting for a Interchange Transaction under different circumstances of current-hour and next-hour schedules and active MW flowing as modified by tag adjust table in E-Tag. 

[image: image11.wmf]MW

Time

10

20

40

S3

S1

TLR

Example 1 – Transaction curtailed, next-hour Energy Profile is higher

	Energy Profile: Current hour
	20 MW

	Actual flow following curtailment: Current hour
	10 MW

	Energy Profile: Next hour
	40 MW


Sub-priorities for Transaction MW:

	Sub-Priority
	MW Value
	Explanation

	S1
	10 MW
	Maintain current curtailed flow

	S2
	+10 MW
	Reload to current hour Energy Profile

	S3
	+20 MW
	Load to next hour Energy Profile

	S4
	


Example 2 – Transaction curtailed, next-hour Energy Profile is lower

	Energy Profile: Current hour
	40 MW

	Actual flow following curtailment: Current hour
	10 MW

	Energy Profile: Next hour
	20 MW


[image: image12.wmf]MW

Time

10

20

40

S2

S1

TLR


Sub-priorities for Transaction MW:

	Sub-Priority
	MW Value
	Explanation

	S1
	10 MW
	Maintain current curtailed flow

	S2
	+10 MW
	Reload to lesser of current and next-hour Energy Profile

	S3
	+0 MW
	Next-hour Energy Profile is 20MW, so no change in MW value

	S4
	


[image: image13.wmf]MW

TLR

Time

10

20

40

S3

S2

S1

Example 3 – Transaction not curtailed, next-hour Energy Profile is higher

	Energy Profile: Current hour
	20 MW

	Actual flow following curtailment: Current hour
	20 MW (no curtailment)

	Energy Profile: Next hour
	40 MW


	Sub-Priority
	MW Value
	Explanation

	S1
	20 MW
	Maintain current flow (not curtailed)

	S2
	+0 MW
	Reload to lesser of current and next-hour Energy Profile

	S3
	+20 MW
	Next-hour Energy Profile is 40MW

	S4
	


[image: image14.emf]00:00 01:00 02:00

:25 :25

IDC results prior

to 00:25 and

01:25 are

not distributed

Example 4 – Transaction not curtailed, next-hour Energy Profile is lower

	Energy Profile: Current hour
	40 MW

	Actual flow following curtailment: Current hour
	40 MW (no curtailment)

	Energy Profile: Next hour
	20 MW


Sub-priorities for Transaction MW:

	Sub-Priority
	MW Value
	Explanation

	S1
	20 MW
	Reduce flow to next-hour Energy Profile (20MW)

	S2
	+0 MW
	Reload to lesser of current and next-hour Energy Profile

	S3
	+0 MW
	Next-hour Energy Profile is 20MW

	S4
	


Example 5 – TLR Issued before Transaction was scheduled to start

	Energy Profile: Current hour
	0 MW

	Actual flow following curtailment: Current hour
	0 MW (Transaction scheduled to start after TLR initiated)

	Energy Profile: Next hour
	20 MW


[image: image15.wmf]MW

Time

10

20

40

S3

TLR

Tag


	Sub-Priority
	MW Value
	Explanation

	S1
	0 MW
	Transaction was not allowed to start

	S2
	+0 MW
	Transaction was not allowed to start

	S3
	+20 MW
	Next-hour Energy Profile is 20MW

	S4
	+0
	Tag submitted prior to TLR


Appendix F. Considerations for Interchange Transactions using Firm Point-to-Point Transmission Service

The following cases explain the circumstances under which an Interchange Transaction using Firm Point-to-Point Transmission Service will be allowed to start as scheduled during a TLR 3b:

Case 1: TLR 3b is called between 00:00 and 00:25 and the Interchange Transaction using Firm Point-to-Point Transmission Service is submitted to IDC by 00:25.

[image: image16.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Firm Transactions

must be submitted

to IDC by 00:25 to

start as scheduled

TLR 3b

IDC issues Congestion

Management Report

based on time of calling

TLR 3b. ADJUST List

follows.

IDC checks for

additional approved

Firm Transactions.

Congestion

Management Report

and second ADJUST

List issued if needed.

TLR 3a

Firm Transactions

that were held are

allowed to start at

02:00

Firm

Transactions in

IDC by 00:25

allowed to start

as scheduled.


1. The IDC will examine the current hour (00) and next hour (01) for all Interchange Transactions.

2. The IDC will issue an ADJUST List based upon the time the TLR 3b is called. The ADJUST List will include curtailments of Interchange Transactions using Non-firm Point-to-Point Transmission Service as necessary to allow room for those Interchange Transactions using Firm Point-to-Point Transmission Service to start as scheduled.

3. At 00:25, the IDC will check for additional Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC by that time and issue a second ADJUST List if those additional Interchange Transactions are found.

4. All existing or new Interchange Transactions using Non-firm Point-to-Point Transmission Service  that are increasing or expected to start during the current hour or next hour will be placed on HALT or HOLD. There is no Reallocation of lower-priority Interchange Transactions using Non-firm Point-to-Point Transmission Service.

5. Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC by 00:25 will be allowed to start as scheduled.

6. Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC after 00:25 will be held.

7. Once the SYSTEM OPERATING LIMIT or INTERCONNECTION RELIABILITY OPERATING LIMIT  Violation is mitigated, the Reliability Authority shall call a TLR Level 3a (or lower). If a TLR Level 3a is called:

a. Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC by 00:25 will be allowed to start as scheduled at 02:00.

b. Interchange Transactions using Non-firm Point-to-Point Transmission Service that were held may then be reallocated to start at 02:00.

Case 2: TLR 3b is called after 00:25 and the Interchange Transaction using Firm Point-[image: image17.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Firm Transactions

must be submitted

to IDC by start of

TLR 3b to start

TLR 3b

IDC issues

Congestion

Management

Report based on

time of calling

TLR 3b. ADJUST

List follows.

Firm Transactions

that are in the IDC

by start of TLR 3b

are started as

scheduled

to-Point Transmission Service is submitted to the IDC no later than the time at which the TLR 3b is called.

1. The IDC will examine the current hour (00) and next hour (01) for all Interchange Transactions.

2. The IDC will issue an ADJUST List at the time the TLR 3b is called. The ADJUST List will include additional curtailments of Interchange Transactions using Non-firm Point-to-Point Transmission Service as necessary to allow room for those Interchange Transactions using Firm Point-to-Point Transmission Service to start at as scheduled.

3. All existing or new Interchange Transactions using Non-firm Point-to-Point Transmission Service that are increasing or expected to start during the current hour or next hour will be placed on HALT or HOLD. There is no Reallocation of lower-priority Interchange Transactions using Non-firm Point-to-Point Transmission Service.

4. Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC by the time the TLR 3b was called will be allowed to start at as scheduled.

5. Interchange Transaction using Firm Point-to-Point Transmission Service that were submitted to the IDC after the TLR 3b was called will be held until the next issuance for TLR (either TLR 3b, 3a, or lower level.)

Case 3. TLR 2 or higher is in effect, a TLR 3b is called after 00:25, and the Interchange Transaction using Firm Point-to-Point Transmission Service is submitted to [image: image18.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Firm Transactions

must be submitted

to IDC by 00:25 to

start as scheduled

Non-firm

Transactions are

Reallocated at

01:00.

TLR 3b

IDC issues

Congestion

Management

Report based on

time of calling TLR

3b. ADJUST List

follows.

IDC checks for

additional approved

Firm Transactions.

Congestion

Management Report

and second ADJUST

List issued if needed.

TLR 3a

Firm

Transactions are

started as

scheduled

the IDC by 00:25.

If TLR 2 or higher has been issued and 3B is subsequently issued, then only those Interchange Transactions using Firm Point-to-Point Transmission Service that had been submitted to the IDC by 00:25 will be allowed to start as scheduled. All other Interchange Transactions are held.

Case 4. TLR 3b is called before 00:25 and the Interchange Transaction is submitted to the IDC by 00:25. TLR 3a is called at 00:40.

[image: image19.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Firm Transactions

must be submitted

to IDC by 00:25 to

start as scheduled

TLR 3b

IDC issues

Congestion

Management

Report based on

time of calling

TLR 3b. ADJUST

List follows.

IDC checks for

additional approved

Firm Transactions.

Congestion

Management Report

and second ADJUST

List issued if needed.

TLR 1

Firm

Transactions are

started as

scheduled. Non-

firm

Transactions

may be loaded.


1. Same as Case 1, but TLR Level 3b ends at 00:40 and becomes TLR Level 3a.

2. All Interchange Transactions using Firm Point-to-Point Transmission Service will start as scheduled if in by the time the 3A is declared.

3. All Interchange Transactions using Non-firm Point-to-Point Transmission Service are reallocated at 01:00.

Case 5. TLR 3b is called before 00:25 and the Interchange Transaction is submitted to the IDC by 00:25. TLR 1 is called at 00:40.


1. Same as Case 1, but TLR Level 3b ends at 00:40 and becomes TLR Level 1.

2. All Interchange Transactions using Firm Point-to-Point Transmission Service will start as scheduled.

3. All Interchange Transactions using Non-firm Point-to-Point Transmission Service may be loaded immediately.

Figure � SEQ Figure \* ARABIC �1� - Timeline showing Approved-tag Submission Deadline for Reallocation





� EMBED Excel.Sheet.8  ���





Figure 5 - IDC report may be run prior to 00:25, but results are not distributed.








� Examples would be 1) a local procedure that curtails Interchange Transactions in a different order or ratio than the Interconnection-wide procedure, or 2) a local re-dispatch procedure.


� The use of PROCEED, CURTAILED, and HOLD refer to an Interchange Transaction status in the IDC, not the E-tag status.


� Flows due to service to Network Customers and Native Load. See “Parallel Flow Calculation Procedure Reference Document.”





Standard Version 0

May 7, 2004
16
Standard Version 0




_1071670800.vsd
Drag the side handles to change the width of the text block.�

�

�

00:00�

01:00�

Potential Adjust List
Issued�

00:20�

00:10�

00:30�

00:40�

00:50�

00:25�

Beginning of
Current Hour�

Approved-Tag Submission
Deadline for Reallocation
(Must be in IDC for
Realloction at 01:00)�

SC Sends Reallocation
notifications. CAs
curtail Non-firm Transactions 
and notify PSEs�

Reallocation begins for Non-firm Transactions that are in IDC by 00:25 and for Firm Transactions that are in by the time the TLR is declared if it is declared after 00:25. Others are held for Reallocation at 02:00.�

TLR Re-issue
Alarm�

Congestion
Management
Report to Issuing
Security Coordinator�

Congestion Management
Report confirmed by Issuing
Security Coordinator�

Congestion
Management
Report confirm by 
Security Coordinator of Sink Control Area�

TLR 3a�

Firm Transactions that are in IDC by 00:25 or by the time the TLR is declared (if later) start as scheduled�

00:35�

Adjust Lists sent to LCAs, GCAs, authoring PSEs�

00:45�

Adjust Tables from 
LCAs�

�


_989837043.xls
Sheet1

				Allocation based on Weighted Impact

				1		2		3		4		5		6		7		8		9

		Transaction ID		Initial Transaction		Distribution Factor		(1)*(2) Impact On Interface		(2)/(2TOT) Impact weighting factor		(3)*(4) Weighted Max Interface Reduction		(5)*(Relief Requested)/(5 Tot) Interface Reduction		(6)/(2) Transaction Reduction		(1)-(7)     New Transaction Amount		(8)*(2) Adjusted Impact On Interface

		Example 1

		A-D(1)		800		0.6		480		0.34		164.57		209.73		349.54		450.46		270.27

		A-D(2)		200		0.6		120		0.34		41.14		52.43		87.39		112.61		67.57

		B-D		800		0.15		120		0.09		10.29		13.11		87.39		712.61		106.89

		C-D		100		0.2		20		0.11		2.29		2.91		14.56		85.44		17.09

		E-B		100		0.05		5		0.03		0.14		0.18		3.64		96.36		4.82

		F-B		100		0.15		15		0.09		1.29		1.64		10.92		89.08		13.36

				2100		1.75		760				219.71		280.00		553.45		1546.55		480.00

		Example 2

		A-D(1)		1000		0.6		600		0.52		313.04		262.16		436.93		563.07		337.84

		B-D		800		0.15		120		0.13		15.65		13.11		87.39		712.61		106.89

		C-D		100		0.2		20		0.17		3.48		2.91		14.56		85.44		17.09

		E-B		100		0.05		5		0.04		0.22		0.18		3.64		96.36		4.82

		F-B		100		0.15		15		0.13		1.96		1.64		10.92		89.08		13.36

				2100		1.15		760				334.35		280.00		553.45		1546.55		480.00

		Example 3

		A-D(1A)		200		0.6		120		0.17		20.28		52.43		87.39		112.61		67.57

		A-D(1B)		200		0.6		120		0.17		20.28		52.43		87.39		112.61		67.57

		A-D(1C)		200		0.6		120		0.17		20.28		52.43		87.39		112.61		67.57

		A-D(1D)		200		0.6		120		0.17		20.28		52.43		87.39		112.61		67.57

		A-D(2)		200		0.6		120		0.17		20.28		52.43		87.39		112.61		67.57

		B-D		800		0.15		120		0.04		5.07		13.11		87.39		712.61		106.89

		C-D		100		0.2		20		0.06		1.13		2.91		14.56		85.44		17.09

		E-B		100		0.05		5		0.01		0.07		0.18		3.64		96.36		4.82

		F-B		100		0.15		15		0.04		0.63		1.64		10.92		89.08		13.36

				2100		3.55		760				108.31		280.00		553.45		1546.55		480.00

				Currently Proposed Method

				1		2		3		4		5		6		7		8		9

				Initial Transaction		Distribution Factor		(1)*(2) Impact On Interface		(3)/(3MAX) Impact weighting factor		(3)*(4) Weighted Max Interface Reduction		(5)*(6 Tot) (5 Tot) Interface Reduction		(6)/(2) Transaction Reduction		(1)-(7)     New Transaction Amount		(8)*(2) Adjusted Impact On Interface

		A-D(1)		800		0.6		480		1.00		480.00		248.27		413.78		386.22		231.73

		A-D(2)		200		0.6		120		0.25		30.00		15.52		25.86		174.14		104.48

		B-D		800		0.15		120		0.25		30.00		15.52		103.44		696.56		104.48

		C-D		100		0.2		20		0.04		0.83		0.43		2.16		97.84		19.57

		E-B		100		0.05		5		0.01		0.05		0.03		0.54		99.46		4.97

		F-B		100		0.15		15		0.03		0.47		0.24		1.62		98.38		14.76

				2100				760		1.58		541.35		280.00		547.39		1552.61		480.00

		A-D(1)		1000		0.6		600		1.00		600.00		268.76		447.94		552.06		331.24

		B-D		800		0.15		120		0.20		24.00		10.75		71.67		728.33		109.25

		C-D		100		0.2		20		0.03		0.67		0.30		1.49		98.51		19.70

		E-B		100		0.05		5		0.01		0.04		0.02		0.37		99.63		4.98

		F-B		100		0.15		15		0.03		0.38		0.17		1.12		98.88		14.83

				2100				760		1.27		625.08		280.00		522.60		1577.40		480.00

		A-D(1A)		200		0.6		120		1.00		120.00		46.32		77.20		122.80		73.68

		A-D(1B)		200		0.6		120		1.00		120.00		46.32		77.20		122.80		73.68

		A-D(1C)		200		0.6		120		1.00		120.00		46.32		77.20		122.80		73.68

		A-D(1D)		200		0.6		120		1.00		120.00		46.32		77.20		122.80		73.68

		A-D(2)		200		0.6		120		1.00		120.00		46.32		77.20		122.80		73.68

		B-D		800		0.15		120		1.00		120.00		46.32		308.79		491.21		73.68

		C-D		100		0.2		20		0.17		3.33		1.29		6.43		93.57		18.71

		E-B		100		0.05		5		0.04		0.21		0.08		1.61		98.39		4.92

		F-B		100		0.15		15		0.13		1.88		0.72		4.82		95.18		14.28

				2100				760		6.33		725.42		280.00		707.64		1392.36		480.00



&L&"Arial,Bold"Southwest Power Pool&C&"Arial,Bold"LLR Scheme Comparison&R&D

Page &P

A

800 (450)

200 (112)

D

B

800 
(713)

C

100 (85)

E

100 (96)

F

100 (89)



Sheet2

		



&A

Page &P



Sheet3

		



&A

Page &P



Sheet4

		



&A

Page &P



Sheet5

		



&A

Page &P



Sheet6

		



&A

Page &P



Sheet7

		



&A

Page &P



Sheet8

		



&A

Page &P



Sheet9

		



&A

Page &P



Sheet10

		



&A

Page &P



Sheet11

		



&A

Page &P



Sheet12

		



&A

Page &P



Sheet13

		



&A

Page &P



Sheet14

		



&A

Page &P



Sheet15

		



&A

Page &P



Sheet16

		



&A

Page &P




