Comment Form

Time Error 

Version 0 Draft 3

WEQBPS-004-000

Posted October 25, 2004 – November 25, 2004

Please submit comment form by November 25, 2004 to:

mailto:naesb@naesb.org, fax: 713-356-0067

Contact Information (Must be Provided)

Contact Name





: Alan Johnson

Comments submitted on Behalf of Organization
: Mirant 

Email of Contact




: alan.r.johnson@mirant.com

Phone Number on Contact



: (678) 579-3108

Comments on Definitions (List comments by Definition)

· With the exception of Leap Second and WECCNet, all of the definitions differ from those contained within NERC’s Version 0 Draft 3 Glossary.  Although I would agree that the “gist” of the definitions is generally the same, I believe that the definitions should be identical to minimize confusion.  Given that the terms are primarily reliability in nature and that the Version 0 concept is “no changes”, NAESB should incorporate the applicable NERC definitions into this business practice. JJD: The NERC and NAESB processes are independent enough that consistency of definitions can never be guaranteed.  However the BPS made every effort to ensure such consistency exists based on definitions available at the time of publication. This should be handled as a maintenance item.
· Proposed definition for WECCNet, which was left blank.

WECCNet – a messaging system used by the Western Electric Coordinating Council (WECC) for use by participating utility’s dispatchers and network administrators. JJD: Recommend incorporating this definition.
Comments on Requirements (List comments by Requirement Number)

1.1 
Current NERC policy calls for notification to the NERC Resources Subcommittee, not the Interconnection Time Monitor.  In the spirit of Version 0 (i.e., no policy changes) suggest either i) substituting Interconnection Time Monitor with NERC Resources Subcommittee or ii) adding “and the NERC Resources Subcommittee” after Interconnection Time Monitor.  JJD: Interconnection Time Monitor was what NERC wanted in place of NERC Resources Subcommittee.
7.0
Suggest replacing this standard with the following language from NERC standard BAL-004-0, R3 that reads as follows: 
“Each Balancing Authority, when requested, shall participate in a Time Error Correction by one of the following methods:” JJD: NERC is not supposed to have this duplicate standard in its Reliability Standards.  However, this wording is an acceptable alternative
7.1 Suggest replacing this standard with the following language from NERC standard BAL-004-0, R3.1 which reads as follows:

“The Balancing Authority shall offset its frequency schedule by 0.02 Hertz, leaving theFrequency Bias Setting normal; or”  JJD: the frequency schedule of 0.02 Hz is a reliability parameter that, according to the NERC/NAESB joint recommendation should not be included in the business practices.  Per that agreement, the business practice can specify the method, but not the actual schedule parameter.
7.2 Suggest replacing this standard with the following language from NERC standard BAL-004-0, R3.2 which reads as follows:

“The Balancing Authority shall offset its Net Interchange Schedule (MW) by an amount equal to the computed bias contribution during a 0.02 Frequency Deviation  (i.e., 20% of the Frequency Bias Setting).” JJD: See 7.2 above.
General Comments

NERC reliability standard BAL-004-0, Time Error Correction, requirement R2, references this NAESB business practice.  As such, it should be compatible with the NERC standard and existing NERC policy (Policy 1D).  Acceptance of the changes proposed above will meet that objective.

Thank you for the opportunity to comment

