Consideration of Comments — 1st Draft of Standard MOD-030-1 Network Response Flowgate ATC (Project 2006-07)

The ATC Standard Drafting Team requesters thank all commenters who submitted comments on the first draft of standard MOD-030-1, Network Response Flowgate ATC (Project 2006-07).  This standard was posted for a 30-day public comment period from May 25 through June 24, 2007.  The requesters asked stakeholders to provide feedback on the standard through a special standard Comment Form. There were 17 sets of comments, including comments from 20 different people from more than 40 companies representing all of the 10 Industry Segments as shown in the table on the following pages. 
Based on the comments received, the drafting team is recommending        .   

In this “Consideration of Comments” document stakeholder comments have been organized so that it is easier to see the responses associated with each question.  All comments received on the standards can be viewed in their original format at: 

http://www.nerc.com/~filez/standards/MOD-V0-Revision.html
If you feel that your comment has been overlooked, please let us know immediately. Our goal is to give every comment serious consideration in this process!  If you feel there has been an error or omission, you can contact the Director of Standards, Gerry Adamski, at 609-452-8060 or at gerry.adamski@nerc.net.  In addition, there is a NERC Reliability Standards Appeals Process.

The Industry Segments are:

1 — Transmission Owners

2 — RTOs, ISOs

3 — Load-serving Entities
4 — Transmission-dependent Utilities

5 — Electric Generators

6 — Electricity Brokers, Aggregators, and Marketers

7 — Large Electricity End Users

8 — Small Electricity End Users

9 — Federal, State, Provincial Regulatory or other Government Entities

10 – Regional Reliability Organizations, Regional Entities

	Commenter
	Organization
	Industry Segment

	
	
	1
	2
	3
	4
	5
	6
	7
	8
	9
	10

	1. 
	Anita Lee (G2)
	AESO
	
	(
	
	
	
	
	
	
	
	

	2. 
	Darrell Pace (G4)
	Alabama Electric Coop. Inc
	
	
	
	(
	(
	(
	
	
	
	

	3. 
	Helen Stines (G4)
	Alcoa Power Generating Inc.
	
	
	
	
	
	(
	(
	(
	
	

	4. 
	Ken Goldsmith (G3)
	ALT
	(
	
	
	
	(
	
	
	
	
	

	5. 
	Eugene Warnecke (G4)
	Ameren
	
	
	(
	
	
	(
	
	
	
	

	6. 
	E. Nick Henery (G1) 
	APPA
	(
	
	
	
	
	
	
	
	
	

	7. 
	Dave Rudolph (G3)
	BEPC
	(
	
	(
	
	(
	(
	
	
	
	

	8. 
	Abbey Nulph (I) 
	BPA 
	(
	
	(
	
	(
	(
	
	
	
	

	9. 
	Brent Kingsford (G2)
	CAISO
	
	(
	
	
	
	
	
	
	
	

	10. 
	Don Reichenbach (G4)
	Duke Energy
	(
	
	(
	
	(
	(
	
	
	
	

	11. 
	Greg Rowland
	Duke Energy
	(
	
	(
	
	(
	(
	
	
	
	

	12. 
	Ed Davis 
	Entergy Services Inc.
	(
	
	(
	
	(
	(
	
	
	
	

	13. 
	George Bartlett 
	Entergy Services Inc.
	(
	
	(
	
	(
	(
	
	
	
	

	14. 
	Jim Case 
	Entergy Services Inc.
	(
	
	(
	
	(
	(
	
	
	
	

	15. 
	Joachim Francois (G4)
	Entergy Services Inc.
	(
	
	(
	
	(
	(
	
	
	
	

	16. 
	Narinder K. Saini 
	Entergy Services Inc.
	(
	
	(
	
	(
	(
	
	
	
	

	17. 
	Steve Myers (I) (G2)
	ERCOT 
	
	(
	
	
	
	
	
	
	
	(

	18. 
	Dave Folk 
	FirstEnergy Corp.
	(
	
	(
	
	(
	(
	
	
	
	

	19. 
	Phil Bowers 
	FirstEnergy Corp.
	(
	
	(
	
	(
	(
	
	
	
	

	20. 
	Richard Kovacs  
	FirstEnergy Corp.
	(
	
	(
	
	(
	(
	
	
	
	

	21. 
	Ross Kovacs (G4)
	Georgia Transmission Co.
	(
	
	(
	
	
	
	
	
	
	

	22. 
	Joe Knight (G3)
	Great River Energy
	(
	
	(
	
	(
	
	
	
	
	

	23. 
	Ron Falsetti (I) (G2)
	IESO
	
	(
	
	
	
	
	
	
	
	

	24. 
	Charles Yeung (G2) 
	IRC
	
	(
	
	
	
	
	
	
	
	

	25. 
	Matt Goldberg (G2)
	ISO New England
	
	(
	
	
	
	
	
	
	
	

	26. 
	Brian Thumm
	ITC
	(
	
	
	
	
	
	
	
	
	

	27. 
	Eric Ruskamp (G3)
	Lincoln Electric System
	(
	
	(
	
	(
	(
	
	
	
	

	28. 
	Michelle Rheault
	Manitoba Hydro EB
	(
	
	(
	
	(
	(
	
	
	
	

	29. 
	Robert Coish (G3)
	Manitoba Hydro EB
	(
	
	(
	
	(
	(
	
	
	
	

	30. 
	Jerry Tang (G4)
	MEAG
	(
	
	(
	
	(
	
	
	
	
	

	31. 
	Tom Mielnik (I) (G3)
	MidAmerican (MEC) 
	(
	
	(
	
	(
	(
	
	
	
	

	32. 
	Dennis Kimm
	MidAmerican (MEC) Trading
	(
	
	(
	
	(
	(
	
	
	
	

	33. 
	Larry Middleton (G4)
	Midwest ISO
	
	(
	
	
	
	
	
	
	
	

	34. 
	Carol Gerou (G3)
	Minnesota Power
	(
	
	(
	
	(
	(
	
	
	
	

	35. 
	Terry Bilke (G3)
	MISO
	
	(
	
	
	
	
	
	
	
	

	36. 
	William Phillips (G2)
	MISO
	
	(
	
	
	
	
	
	
	
	

	37. 
	Jim Castle (G2)
	New York ISO
	
	(
	
	
	
	
	
	
	
	

	38. 
	Matt Schull (G1)
	North Carolina MPA
	
	
	(
	(
	(
	(
	
	
	
	

	39. 
	Todd Gosnell (G3)
	OPPD
	(
	
	(
	
	
	(
	
	
	
	

	40. 
	Alicia Daugherty (G2)
	PJM
	
	(
	
	
	
	
	
	
	
	

	41. 
	C. Robert Moseley (G5)
	PSC of South Carolina
	
	
	
	
	
	
	
	
	(
	

	42. 
	David A. Wright (G5)
	PSC of South Carolina
	
	
	
	
	
	
	
	
	(
	

	43. 
	G. O'Neal Hamilton (G5)
	PSC of South Carolina
	
	
	
	
	
	
	
	
	(
	

	44. 
	John E. Howard (G5)
	PSC of South Carolina
	
	
	
	
	
	
	
	
	(
	

	45. 
	Mignon L. Clyburn (G5)
	PSC of South Carolina
	
	
	
	
	
	
	
	
	(
	

	46. 
	Phil Riley (G5)
	PSC of South Carolina
	
	
	
	
	
	
	
	
	(
	

	47. 
	Randy Mitchell (G5)
	PSC of South Carolina
	
	
	
	
	
	
	
	
	(
	

	48. 
	Chuck Falls
	Salt River Project (SRP)
	(
	
	(
	
	(
	(
	
	
	
	

	49. 
	Al McMeekin (G4)
	SC Electric & Gas Co.
	
	
	(
	
	(
	(
	
	
	
	

	50. 
	Stan Shealy (G4)
	SC Electric & Gas Co.
	
	
	(
	
	(
	(
	
	
	
	

	51. 
	Bryan Hill (G4)
	SCS- Trans
	(
	
	
	
	(
	
	
	
	
	

	52. 
	DuShaune Carter (G4)
	SCS -Trans
	(
	
	
	
	(
	
	
	
	
	

	53. 
	John Troha (G4)
	SERC ATCWG
	
	
	
	
	
	
	
	
	
	(

	54. 
	Carter Edge (G4)
	SERC RC
	
	
	
	
	
	
	
	
	
	(

	55. 
	W .Shannon Black (G5)
	SMUD
	(
	
	(
	
	(
	(
	
	
	
	

	56. 
	Doug Bailey (G4)
	TVA
	(
	
	(
	
	(
	
	
	
	
	

	57. 
	Jim Haigh (G3)
	WAPA
	(
	
	
	
	
	(
	
	
	
	

	58. 
	Neal Balu (G3)
	WPS
	
	
	(
	
	(
	(
	
	
	
	

	59. 
	Pam Oreschnick (G3)
	XEL
	(
	
	(
	
	(
	(
	
	
	
	


I – Indicates that individual comments were submitted in addition to comments submitted as part of a group

G1 – APPA
G2 – ISO – RTO Standards Review Committee
G3 – MRO Members (MRO)
G4 – SERC Available Transfer Capability Working Group (SERC ATCWG)
G5 – PSC of South Carolina

Index to Questions, Comments, and Responses
51.
Do you agree with the responsible entities described in Requirements four through seven and eleven (R4-R7 and R11)?   If “No,” please explain why in the comments area.


72.
Do you believe that all elements of ETC have been adequately captured in Requirements fourteen and eighteen (R14 and R18)?  If “No,” please explain why in the comments area.


113.
Is the conversion of AFC to ATC adequately described in Requirement twenty-two (R22)? If “No,” please explain why in the comments area.


134.
Do you anticipate any problems with posting both AFCs and ATCs as described in Requirements twenty-one and twenty-four (R21 and R24) in this draft standard?  If “Yes,” please explain why in the comments area.


155.
The drafting team attempted to address all of the directives identified in the Federal Energy Regulatory Commission’s (FERC) Orders 890 and 693 related to AFC, as it relates to ATC.  Do you agree that the drafting team has adequately responded to all of FERC’s directives in FERC Orders 890 and 693 related to AFC in this draft of MOD-030-1?  If “No,” please explain why in the comments area.


176.
Do you agree with the functional entities identified in the “Applicability” section of the draft standard?  If “No,” please identify the functional entities to whom you believe the standard should apply and why.


197.
In R15, we provided a preliminary response to Order 890s paragraph 245, which deals with reservations that have the same POR (generator) but different PODs (loads).  Do you agree that R15 meets the intent of order 890?  If “No,” please suggest how you believe the Order’s requirements from paragraph 245 should be addressed in the comments area.


228.
Do you agree with the 3% specified in R16 for including third party impacts?  If “No,” please specify what percent or alternate approach should be used and explain why in the comment area below.


259.
Are you aware of any conflicts between the proposed standard and any regulatory function, rule/order, tariff, rate schedule, legislative requirement or agreement?  If “Yes,” please the conflict in the comments area.


2710.
Please provide any other comments (that you have not already provided in response to the questions above) that you have on the draft standard MOD-030-1.





1. Do you agree with the responsible entities described in Requirements four through seven and eleven (R4-R7 and R11)?   If “No,” please explain why in the comments area.

Summary Consideration:  

	Question #1

	Commenter
	Yes
	No
	Comment

	SMUD
	
	(
	"Planning Coordinator" is not a defined term.  Pleae correct.

	Response: 

	APPA
	
	(
	These requirements should be in the FAC series and developed by personnel who are experienced in the determination of flowgates and their limitations.  The requirements, as written are requiring improper use of the values stated in the requirements.

	Response: 

	BPA
	
	(
	"Planning Coordinator" is not defined in the NERC Glossary of Terms Used in Reliability Standards.  Please clarify what the Planning Coordinator is or replace "Planning Coordinator" with Planning Authority.

	Response: 

	Entergy
	
	(
	R5 reference to Transmission Operator should be changed to Transmission Owner.

	Response: 

	ERCOT
	(
	
	See IRC comments submitted by Charles Yeung.

	Response: 

	FirstEnergy 
	(
	
	

	IESO
	(
	
	

	ISO SC
	(
	
	

	ITC
	
	(
	ITC agrees with the requirements, themselves, but disagrees with the responsible entities.  The Transmission Owner and/or Transmission Operator should be responsible for determing all limits (thermal, voltage, stability) of the transmission facilities.  The TO/TOP may choose to delegate the activities, but the requirements in this Standard have put the responsibility on the wrong entity.  The RC should not be involved in the determination of facility limits unless so designated to do so.  R4 and R5 are appropriate in that respect, but the others are not.  As a Transmission Owner/Operator, ITC would be object to any rating greater than one we would provide.  This is a dangerous possibility as currently written particularly if commericial interests could affect reliability considerations.

	Response: 

	MEC Trading
	
	
	The functional model doesn't necessarily translate to reality so this is hard to answer.

	Response:

	MEC
	
	(
	For R6, R8, R9, R10, R11 the responsible entities described are incorrectly based upon the assumption that all NERC members are members of an RTO.  These requirements should be revised in this regard to provide that "the Transmission Service Provider, the Reliability Coordinator, and/or the Planning Coordinator, as appropriate", do these requirements in the standard.  Further R1 and R2 should also be revised for this reaons to also refer to the "Transmission Service Provider, the Reliabiltiy Coordinator and/or the Planning Coordinator, as appropriate."

	Response:

	Manitoba Hydro
	(
	
	

	MRO
	
	(
	The MRO believes that for R6, R8, R9, R10, R11 the responsible entities described are incorrectly based upon the assumption that all NERC members are members of an RTO.  These requirements should be revised in this regard to provide that "the Transmission Service Provider, the Reliability Coordinator, and/or the Planning Coordinator, as appropriate", do these requirements in the standard.  Further R1 and R2 should also be revised for this reaons to also refer to the "Transmission Service Provider, the Reliabiltiy Coordinator and/or the Planning Coordinator, as appropriate."

	Response:

	PSC SC
	(
	
	

	SERC ATCWG
	
	(
	See answer to #6.  

	Response:


2. Do you believe that all elements of ETC have been adequately captured in Requirements fourteen and eighteen (R14 and R18)?  If “No,” please explain why in the comments area.  


Summary Consideration:  

	Question #2

	Commenter
	Yes
	No
	Comment

	SMUD
	
	(
	The impact of load growth for Network Integration Transmission Service should be included in the second sub-bullet of R14.

The "five years or longer in duration" language should be removed from the fifth sub-bullet of R14. due to the fact that this element of Order 890 is only to be implemented by a TSP once the FERC has approved the TSP's Attachment K -- this may not occur for some TSPs until after the standards are to be implemented.  Additionally, regardless of whether a TSP's Attachment K is approved, there will be a transition period (to be developed by each TSP) from the old 1-year/60-day roll-over paradigm to the 5-year/1-year -- the standard should not preclude a TSP from encumbering capacity for those exisitng Customers who have not yet been required to commit to five years of service to retain their roll-over rights.

	Response: 

	APPA
	
	(
	These requirements are tariff or contract requirements that will be contained in or a part of a regulatory or legal document.  Some of these requirements are not a reliability issues since and should be removed.  Those statements that want to know the effects of actions that are of a reliability nature will be determined by other functions not the TSP, which just sell transmission capacity.

	Response: 

	BPA
	
	(
	The impact of load growth for Network Integration Transmission Service should be included in the second sub-bullet of R14.  

The "five years or longer in duration" language should be removed from the fifth sub-bullet of R14. due to the fact that this element of Order 890 is only to be implemented by a Transmission Service Provider (TSP) once the FERC has approved the TSP's Attachment K -- this may not occur for some TSPs until after the standards are to be implemented.  Additionally, regardless of whether a TSP's Attachment K is approved, there will be a transition period (to be developed by each TSP) from the old 1-year/60-day roll-over paradigm to the 5-year/1-year -- the standard should not preclude a TSP from encumbering capacity for those existing Customers who have not yet been required to commit to five years of service to retain their roll-over rights. 

The ninth sub-bullet should include all other impacts and not just the impacts using transmission service to service Native Load or firm Network Integration load.  Therefore, "using transmission that serves Native Load or Firm Network Integration Transmission Service" should be deleted.

	Response: 

	Entergy
	(
	
	Sub requirements shown as bullets should be changed to numbered subrequirements in R14, R16 and R18.

	Response: 

	ERCOT
	
	(
	See IRC comments submitted by Charles Yeung.

	Response: 

	FirstEnergy
	(
	
	However, the term "Post-backs" is industry jargon and should be replaced with the term "reinstatement" to add clarity.

	Response: 

	IESO
	
	(
	R14: It is not clear if the standard requires all inputs to be included in the calculation of the impact of Firm ETC.  If so, 2 of bullet points are questionable:

• FIRM NITS Reservations (second bullet point) are only explicitly incorporated in ETC if they cross control area boundaries. (POR not equal to POD) Otherwise they are part of the base-flow calculations - Designated Network Resources (DNRs) serving Native Load (first bullet point). In order to clarify, we could add  to the second bullet: "not otherwise included in TRM or CBM  or in the impacts of Native Load commitments"

• Impact of Ancillary Services not included already in TRM, is very difficult to quantify and include in ETC.
R18

• Non-Firm ETC calculations use the same base flow based on resources serving native load commitments as Firm ETC Calculations. Non-Firm  NITS Reservations (second bullet point) are only explicitly incorporated in ETC if they cross control area boundaries (POR not equal to POD). Otherwise they are part of the base-flow calculations.

	Response: 

	IRC
	
	(
	R14:

It is not clear if the standard requires all inputs to be included in the calculation of the impact of Firm ETC.  If so, 2 of bullet points are questionable:

•    FIRM NITS Reservations (second bullet point) are only explicitly incorporated in ETC if they cross control area boundaries. (POR not equal to POD) Otherwise they are part of the base-flow calculations,  DNR’s serving Native Load. (first bullet point).  Maybe add to second bullet:  not otherwise included in TRM or CBM  or in the impacts of Native Load commitments of first bullet point.

•    Impact of Ancillary Services not included already in TRM, is very difficult to quantify and include in ETC.

R18

•    Non-Firm ETC calculations are using same base flow based on Resources serving Native Load commitments as Firm ETC Calculations.   The base flow calculations don’t make a distinguishion between Non-Firm or Firm,  only if part of the Native Load is supplied by DNR from outside the Control Area.  Non-Firm  NITS Reservations (second bullet point) are only explicitly incorporated in ETC if they cross control area boundaries. Otherwise they are part of the base-flow calculations.  

	Response: 

	ITC
	
	(
	It is not clear that any "allocations" of flowgate capacity, such as in the MISO/PJM Seams agreement, are covered here.  These allocations, while technically covered by the 2nd to last bullet, need to be addressed by stronger language than a blanket "any other agreements" clause.

	Response: 

	MEC Trading
	(
	
	

	MEC
	
	(
	1.  R1.1, R3, R11and other requirements that indicate that the results are to be made available publicly should indicate that these results should be made available publicly "on the OASIS" so that this information is not made publicly without registration.  2.  R14 should be revised to indicated that "The Transmission Service Provider shall determine the impact of firm ETCs based on "an appropriate level of " the following inputs.  3.  R16 the impacts by more than 3% are consistent with post-contingent flowgates.  It should be noted that there are continuing to exist in the area, pre-contingent flowgates which would be inproperly represented by post-contingent flowgates.  The pre-contingent flowgates in the area generally only consider signficant third-party impacts that are at 5% or more.  Therefore, provisions should be made in R16 to allow the appropriate screen, 3% or 5%, for the appropriate type of flowgate, post-contingent or pre-contingent.  4.  R18 should be expanded to include the use of metered data to forecast non-firm ETC in the operating horizon and therefore, allowing the release of non-firm ETC for non-firm ATCs in the operating horizon.  This method is being used in the area to maximize the non-firm offerings in the operating horizon.  I suggest wording such as the following for R18 or as a subrequirement:  "Forecasts of non-firm ETC may be made using metered data so as to allow the release of non-firm ETC in the operating horizon.  When such forecasting methods are used, it may be assumed that reductions in metered flows in the operating horizon are due to reductions in non-firm ETC."  5.  Either use existing transmission commitments in lower case or else provide a definition for the NERC Glossary.

	Response:

	Manitoba Hydro
	(
	
	

	MRO
	
	(
	1.  R1.1, R3, R11and other requirements that indicate that the results are to be made available publicly should indicate that these results should be made available publicly "on the OASIS" so that this information is not made publicly without registration.  2.  R14 should be revised to indicated that "The Transmission Service Provider shall determine the impact of firm ETCs based on "an appropraite level of " the following inputs.  3.  R16 the impacts by more than 3% are consistent with post-contingent flowgates.  It should be noted that there are continuing to exist in the MRO area, pre-contingent flowgates which would be inproperly represented by post-contingent flowgates.  The pre-contingent flowgates in the MRO generally only consider signficant third-party impacts that are at 5% or more.  Therefore, provisions should be made in R16 to allow the appropriate screen, 3% or 5%, for the appropriate type of flowgate, post-contingent or pre-contingent.  4.  R18 should be expanded to include the use of metered data to forecast non-firm ETC in the operating horizon and therefore, allowing the release of non-firm ETC for non-firm ATCs in the operating horizon.  This method is being used in the MRO to maximize the non-firm offerings in the operating horizon.  The MRO suggests wording such as the following for R18 or as a subrequirement:  "Forecasts of non-firm ETC may be made using metered data so as to allow the release of non-firm ETC in the operating horizon.  When such forecasting methods are used, it may be assumed that reductions in metered flows in the operating horizon are due to reductions in non-firm ETC."  5.  Either use existing transmission commitments in lower case or else provide a definition for the NERC Glossary.

	Response:

	PSC SC
	(
	
	

	SERC ATCWG
	(
	
	


3. Is the conversion of AFC to ATC adequately described in Requirement twenty-two (R22)? If “No,” please explain why in the comments area.  


Summary Consideration:  

	Question #3

	Commenter
	Yes
	No
	Comment

	APPA
	
	(
	Need to let the expanded SDT review this by personnel knowledgeable in development of AFT and distribution factors

	Response: 

	BPS
	(
	
	However, for the reasons explained in our response to the MOD-030-1 Comment Form's question 4, BPA suggests that R22. be modified to the following:

" The Transmission Service Provider shall make publicly available a mechanism for interested parties to convert Flowgate AFCs to path ATCs based on…"

	Response: 

	Entergy
	
	(
	The requirement should be worded in simple language to reflect how AFCs are determined rather than an equation that a program can use in developing program.

	Response: 

	ERCOT
	(
	
	See IRC comments submitted by Charles Yeung.

	Response: 

	FirstEnergy
	(
	
	

	IESO
	(
	
	Yes, the conversion is described adequately. In the first bullet point, "…the Transmission Service Provider shall calculate the partial AFC of that…" should be written as "…the Transmission Service Provider shall calculate the partial ATC of that…"

	Response: 

	IRC
	(
	
	Yes, conversion described adequate.

•  Partial AFC should be partial ATC in first bullet point.

	Response: 

	ITC
	
	(
	The conversion of AFC to ATC is covered, but it is not clear.  The original SAR for this standard included a white paper with appropriate coversion formulae.  Please consult and include the translation equations.

	Response: 

	MEC Trading
	(
	
	

	MEC
	
	(
	The R22 is inadequate in describing what must be done.  It is unclear what path the flowgates are to be converted to.  Are the flowgate quantities to be converted into equivalent control area to control area path quantities?  Are the flowgate quantities to be converted into flowgate path quantities?  If it is the latter, what are the definitions and purposes of the flowgate path quantities?  In addition, I do not understand what the benefits are in converting Flowgate AFCs to path AFCs.  It seems to be an unnecessary and confusing requirement albeit one in FERC Order 890.

	Response: 

	Manitoba Hydro
	
	(
	I don't believe there should be a conversion it only leads to uncertainty. I believe that the committee should be able to standardize on one technique.

	Response:

	MRO
	
	(
	The MRO believes that the R22 is inadequate in describing what must be done.  It is unclear what path the flowgates are to be converted to.  Are the flowgate quantities to be converted into equivalent control area to control area path quantities?  Are the flowgate quantities to be converted into flowgate path quantities?  If it is the latter, what are the definitions and purposes of the flowgate path quantities?  In addition, the MRO does not understand what the benefits are in converting Flowgate AFCs to path AFCs.  It seems to be an unnecessary and confusing requirement albeit one in FERC Order 890.

	Response:

	PSC SC
	(
	
	

	SERC ATCWG
	
	(
	The definition provided in the SAR was clearer than the current definition.  The new definition introduces new terms into the process that are not industry standard or recognizable.

	Response:


4. Do you anticipate any problems with posting both AFCs and ATCs as described in Requirements twenty-one and twenty-four (R21 and R24) in this draft standard?  If “Yes,” please explain why in the comments area.   


Summary Consideration:  

	Question #4

	Commenter
	Yes
	No
	Comment

	SMUD
	(
	
	(The below statement is proposed by BPA.  Is the WECC Team OK with supporting it?) 

Under the flowgate methodology, ATC is a value derived from an analysis of the expected powerflow impacts of a reservation across multiple flowgates.  Consequently, it is the posting of AFC and timely posting of changes to AFC that inform whether transfer capability exists to support a request for transmission service.  ATC for a POR-POD path is derived from posted AFC.  When posting both ATC by path as well as AFC by flowgate, there is a risk that the AFC and ATC values could get "out of sync" due to automation lag-time, etc.  BPA believes that greater consistency and transparency is achieved if only AFC values are posted for each flowgate, and requestors are provided with a "conversion calculator" that calculates ATC for their requested path based on posted AFC's.

	Response: 

	APPA
	(
	
	This Standard trys to provide detail requirements for AFT, ATC, ETC and the requirements of 3 different functional entities and it is written in a manner that will not support a Compliance program.

	Response: 

	BPA
	(
	
	Under the flowgate methodology, ATC is a value derived from an analysis of the expected powerflow impacts of a reservation across multiple flowgates.  Consequently, it is the posting of AFC and timely posting of changes to AFC that inform whether transfer capability exists to support a request for transmission service.  ATC for a POR-POD path is derived from posted AFC.  When posting both ATC by path as well as AFC by Flowgate, there is a risk that the AFC and ATC values could get "out of sync" due to automation lag-time, etc.  BPA believes that greater consistency and transparency is achieved if only AFC values are posted for each Flowgate, and requestors are provided with a "conversion calculator" that calculates ATC for their requested path based on posted AFC's.

	Response: 

	Entergy
	
	(
	AFCs are not required to be posted as these do not mean much to the users, therefore, R21 should be deleted.

	Response: 

	ERCOT
	(
	
	See comment 9.

	Response: 

	FirstEnergy
	(
	
	The standard should include specifics of methods for complying with the term "publicly available" such as posting on OASIS, a corporate web page, etc. (This concept is mentioned in all MOD-028, MOD-029, and MOD-030.)

	Response: 

	IESO
	(
	
	R21 and R24

Current tools allow the submission of requests and retrieval of available and calculated AFC and ATC data. It is questionable if that is considered being compliant with R21 and R24.   If not,  changes to the software might be required to meet the requirements of R21 and R24.

	Response: 

	IRC
	(
	
	R21 and R24

Current tools allow to submit test requests and get AFC and ATC data available. It is questionable if that is considered being compliant with R21 and R24.   If not,  changes to software are required to meet the requirements of R21 and R24.

	Response: 

	ITC
	(
	
	A ridiculous amount of paper or web space will be used if all ATC path values are posted for large footprints.  Flowgates can be in the thousands but ATC paths are quadratic functions of the number of Sources/Sinks (i.e., too many paths to print).   ATC for a given path should be on request.  (i.e., ask for the path and the TSP provides that specific path ATC via OASIS).  This should be either through manual entry by the requestor or electronically via a requestor electronic query tool (i.e., computer program query).

	Response: 

	MEC
	(
	
	It will be incredibly confusing posting both AFCs and ATCs for the same transmission service.  I agree that this is in accordance with the FERC Order 890; however, I do not understand what the benefits of this conversion to open transmission service and reliability.  I ask the SDT to clarify.

	Response: 

	MRO
	(
	
	It will be incredibly confusing posting both AFCs and ATCs for the same transmission service.  The MRO agrees that this is in accordance with the FERC Order 890; however, the MRO does not understand what the benefits of this conversion to open transmission service and reliability.  The MRO asks the SDT to clarify.

	Response:

	PSC SC
	
	(
	

	SERC ATCWG
	(
	
	Posting the AFC numbers provide no additional value if the ATC numbers are posted.

	Response:


5. The drafting team attempted to address all of the directives identified in the Federal Energy Regulatory Commission’s (FERC) Orders 890 and 693 related to AFC, as it relates to ATC.  Do you agree that the drafting team has adequately responded to all of FERC’s directives in FERC Orders 890 and 693 related to AFC in this draft of MOD-030-1?  If “No,” please explain why in the comments area. 


Summary Consideration:  

	Question #5

	Commenter
	Yes
	No
	Comment

	APPA
	
	(
	The Federal Energy Regulatory Commission (FERC) has requested Standards that determine the requirements to calculate TTC will be handled in the FAC Standards.  Order 693 States the following: 1050. We adopt the NOPR proposal and require that TTC be addressed under the Reliability Standard that deals with transfer capability such as FAC-012-1, rather than MOD-001-0. The FAC series of standards contain the Reliability Standards that form the technical and procedural basis for calculating transfer capabilities. FAC-008-1 provides the basis for determining the thermal ratings of facilities while FAC-009-1 provides the basis for communicating those ratings. FAC-010-1 and FAC-011-1 provide the system operating limits methodologies for the planning and operational horizon respectively and FAC-014 provides for the communication of those ratings. FERC has correctly recognized that FAC-012 and FAC-013, while associated with modeling is highly dependent on the previous FAC Standards as noted by FERC.

	Response: 

	Duke
	
	(
	Conditional Firm Service (CFS) and Planning Redispatch Service (PRS) under Order No. 890 create new issues relating to modeling and calculating ATC.  Specifically, when PRS is offered to maintain service, modeling for ATC calculations will be impacted during these periods.  TTC must be modeled/calculated accounting for the new CFS/PRS requirements.

	Response: 

	Entergy
	(
	
	

	ERCOT
	
	(
	See IRC comments submitted by Charles Yeung.

	Response: 

	FirstEnergy
	(
	
	

	IESO
	
	(
	Note - We don’t have a complete overview of all directives to answer this question.

	Response: 

	IRC
	
	(
	Note - Don’t have a complete overview of all directives to answer that question. This is time intensive!!!!

	Response: 

	MEC Trading
	
	(
	Standard is a fill-in-the-blank

	Response: 

	MEC
	(
	
	

	MRO
	(
	
	

	PSC SC
	(
	
	


6. Do you agree with the functional entities identified in the “Applicability” section of the draft standard?  If “No,” please identify the functional entities to whom you believe the standard should apply and why. 


Summary Consideration:  

	Question #6

	Commenter
	Yes
	No
	Comment

	SMUD
	
	
	See above on defining Planning Coordinatior.

	Response: 

	BPA
	
	(
	"Planning Coordinator" is not defined in the NERC Glossary of Terms Used in Reliability Standards.  Please clarify what the Planning Coordinator is or replace "Planning Coordinator" with Planning Authority.

	Response: Planning Coordinator is a new name for the entity Planning Authority in Functional Model.  SDT will recommend to add a new definition for Planning Coordinator to the glossary of terms in NERC Standards booklet.

	Entergy
	(
	
	

	ERCOT
	
	(
	See IRC comments submitted by Charles Yeung.

	Response: See response to IRC comments submitted by Charles Yeung.

	FirstEnergy
	(
	
	MOD-001, 028, 029, and 030 should be combined into one standard to eliminate the need to reference several standards at once, eliminate duplication, and simplify the applicability sections of MOD-028, 029, and 030

	Response: SDT decided to split these standards based on comments received on earlier posting.

	IESO
	
	(
	TSP is the sole entity responsible for performing calculations, and posting of the results. The  PC, RC, and TO only submit data to the TSP, such as list of OTDF and PTDF flow gates, seasonal limits of flow gates, flowgate components, flow directions on flowgate components etc. They do not calculate ATC, hence R1 is irrelevant.

	Response: SDT needs to decide about what role PC, RC, and TO has in R1. 

	IRC
	
	(
	TSP is responsible to perform calculations, and post the results,  the  PC and RC and TO only submit data to TSP, such as list of flow gates, limits of flow gates. They do not calculate ATC, hence R1 is irrelevant.

	Response: SDT needs to decide about what role PC, RC, and TO has in R1

	ITC
	
	(
	Applicable Entity 4.2  is not appropriate.  Reliability Coordinators should not be calculating ATC.  According to the Functional Model, ATC Calculations are performed by the Transmission Service Provider (Task #2, "Determine and post available transfer capability values.")   R4 and R5 identify the TO and TP as responsible entities, and need to be included in the applicability sections.

	Response: SDT needs to decide what roles RC should play in AFC calculations.  SDT will add TO and TP to Applicable entity in view of R4.

	MEC
	
	(
	It is not appropriate to qualify the Functional Entity as provided in A.4.1 through A.4.3, that is, A.4.1 through A.4.3 should just list the NERC functions from the NERC functional model and not qualify it.   For example, 4.1 should be "Planning Coordinator" not "Each Planning Coordinator that uses the Flowgate Network Response method to calculate…..".  Then it is up to Planning Coordinators etc. to review the standard to see how the requirements are to be applied, if at all.    

	Response: SDT shall remove the qualifications to be consistent with other standards.

	Manitoba Hydro
	(
	
	

	MRO
	
	(
	The MRO believes it is not appropriate to qualify the Functional Entity as provided in A.4.1 through A.4.3, that is, the MRO recommends that A.4.1 through A.4.3 just list the NERC functions from the NERC functional model and not qualify it.   For example, 4.1 should be "Planning Coordinator" not "Each Planning Coordinator that uses the Flowgate Network Response method to calculate…..".  Then it is up to Planning Coordinators etc. to review the standard to see how the requirements are to be applied, if at all.

	Response: SDT shall remove the qualifications to be consistent with other standards.

	PSC SC
	(
	
	

	SERC ATCWG
	
	(
	The applicability section needs clarification.  Referencing R1,6,8,9 and 10 they should apply only to those entities performing the function.  The standard should not require the calculations be made by the PC and RC, but should be applicable to the designated entitiy performing these calculations .  The designated entity must be specified as a requirement in this standard.  For example: The TSP, PC and RC must specify and agree to the entity that performs this function in the TSP’s ATCID as required in MOD 1.   The current revision of MOD-001 states the following requirement as R1:  “Each Transmission Service Provider, and its associated Planning Coordinators and Reliability Coordinators, shall agree upon and implement one or more of the ATC methodologies specified in Reliability Standard MOD-028, MOD-029, and MOD-030 for use in determining Transfer Capabilities of those Facilities under the tariff administration of that Transmission Service Provider.”  The requirements of MOD-0028 should refer to the Designated Entity specified through this requirement.  The following are examples of how this would be implemented in the standard:

B. Requirements

R4. Each Designated Entity shall ensure that the Total Transfer Capability (TTC) for each of its Transmission Service Provider’s POR to POD Paths is calculated and up-to-date for use within the Transfer Capability time horizons specified in MOD-001 R2.

R5. Prior to calculating TTC, each Designated Entity shall update the following components of the base case power flow model it uses to calculate TTC for the time horizon being studied:

	Response: SDT shall develop appropriate response.


7. In R15, we provided a preliminary response to Order 890s paragraph 245, which deals with reservations that have the same POR (generator) but different PODs (loads).  Do you agree that R15 meets the intent of order 890?  If “No,” please suggest how you believe the Order’s requirements from paragraph 245 should be addressed in the comments area.

Summary Consideration:  

	Question #7

	Commenter
	Yes
	No
	Comment

	SMUD
	(
	
	

	Entergy
	(
	
	

	ERCOT
	
	(
	See IRC comments submitted by Charles Yeung.

	Response: See response to IRC comments submitted by Charles Yeung.

	FirstEnergy
	(
	
	However, the phrase "not exceed" can be replaced with the word "the" since the term "limiting the total impact" is synonomous.

	Response: SDT shall modify standard to reflect comment regarding change in the language.

	IESO
	
	(
	No. R15 doesn’t meet the intend of paragraph 245.  Most of the PtP Reservations don’t have specific resources as Source, they typically source from a group of commonly dispatched units.   Also  most Tariff’s allow re-direct of Reservations to different Sources, so excluding Reservations from impact calculations could possibly result in overselling the system if the excluded reservation is re-directed to a different source. It might be possible to make some general guidelines to address the paragraph 245 of Order 890 such as:

• Total sum of Reservations (Confirmed, Approved, Study)  impacting a specific corridor, such as a DC tie should not exceed the total capacity of the corridor.

• Total sum of Reservations (Confirmed, Approved, Study) sinking in a Control Area should not exceed the total Load of the Control Area.

• Total sum of Reservations ((Confirmed, Approved, Study) sourcing from a group of commonly dispatched units should not exceed the total available generation capacity of that group of units.  

	Response: SDT addressed FERC Order 890 requirement, alternative language does not directly address the FERC requirements.  FERC did not require limiting reservations, it just require to limit the use/impact not to exceed the name plate rating of generators used as POR.

	IRC
	
	(
	No R15 doesn’t meet the intend of paragraph 245.  Most of the PtP Reservations don’t have specific resources as Source, they typically source from a group of commonly dispatched units.   Also  most Tariff’s allow re-direct of Reservations to different Sources, so excluding Reservations from impact calculations could possibly result in overselling the system if the excluded reservation is re-directed to a different source. It might be possible to make some general guidelines to address the paragraph 245 of Order 890 such as:

•
Total sum of Reservations (Confirmed, Approved, Study)  impacting a specific corridor, such as a DC tie should not exceed the total capacity of the corridor.

•
Total sum of Reservations (Confirmed, Approved, Study) sinking in a Control Area should not exceed the total Load of the Control Area.

•
Total sum of Reservations ((Confirmed, Approved, Study) sourcing from a group of commonly dispatched units should not exceed the total available generation capacity of that group of units.

	Response: DT addressed FERC Order 890 requirement, alternative language does not directly address the FERC requirements.  FERC did not require limiting reservations, it just require to limit the use/impact not to exceed the name plate rating of generators used as POR.

	ITC
	
	(
	It meets the intent but is subject to potentiallt adverse interpretation.  It is true that a POR may not exceed Pmax for the installed generation; however, when multiple requests are received  for the POR that exceed Pmax, should the requests be taken first-come-first-served until Pmax is reached?  Should the worst-case scenario be studied and used to set limits?  Should the requests be pro-rated until the sum of the requests is reduced to Pmax?  We believe the TSP should be allowed some leeway in how they model these situations, in order to prevent reliability problems.

	Response: R5 is not intended to limit transmission service requests but to limit their impact not to exceed the name plate rating of generators.  

	MEC Trading
	(
	
	The words meet the intent of the order, but the order may not be technically correct, nor consistent with other OATT requirements.

	Response: No Comment.

	MEC
	(
	(
	The words seem to meet the requirement although developing a process which meets the requirment is very difficult to do.  Also, this requirement is a transmission service request evaluation process requirement and does not belong in its present form in a standard concerning ATCs calculation.  Also, there are issues with implementing this requirement.  When there are numerous point to point requests for transmission service where some of them are partial path requests, it is not clear how to enforce the impacts of all transmission service shall not exceed the source at a particular point.  If the Standards Drafting Team intends to continue with this requirement, the Standards Drafting Team should outline some subrequirements which explain how the Transmission Service Provider is to do this.  It would be helpful if the SDT would develop an example of multiple requests some of which are partial path requests to the source point where subsequent requests will result in power being moved away from the point and show how the Transmission Service Provider than reviews the impacts to meet the requirement.

	Response: SDT SHARES YOUR PAIN!!!!

	MRO
	(
	(
	The words seem to meet the requirement although developing a process which meets the requirment is very difficult to do.  Also, this requirement is a transmission service request evaluation process requirement and does not belong in its present form in a standard concerning ATCs calculation.  Also, there are issues with implementing this requirement.  When there are numerous point to point requests for transmission service where some of them are partial path requests, it is not clear how to enforce the impacts of all transmission service shall not exceed the source at a particular point.  If the Standards Drafting Team intends to continue with this requirement, the Standards Drafting Team should outline some subrequirements which explain how the Transmission Service Provider is to do this.  It would be helpful if the SDT would develop an example of multiple requests some of which are partial path requests to the source point where subsequent requests will result in power being moved away from the point and show how the Transmission Service Provider than reviews the impacts to meet the requirement.

	Response: SDT SHARES YOUR PAIN!!!!

	PSC SC
	(
	
	


8. Do you agree with the 3% specified in R16 for including third party impacts?  If “No,” please specify what percent or alternate approach should be used and explain why in the comment area below.   

Summary Consideration:  

	Question #8

	Commenter
	Yes
	No
	Comment

	SMUD
	
	(
	The threshold of 3% appears to be an arbitrary level.  This level may be rooted in Operational and Planning studies that consider impacts from outages on one TP's system that increase loading on an element of another TP's system by 3% or more.  While this level may be a good indicator of impact, it may not provide an indicator of which party's ownership or allocation of facilities is being used.  It does not assure TPs will be able to preserve their rights (i.e. by contractual allocation) with a fixed threshold of 3%.

	Response: SDT needs to review and respond.

	BPA
	
	(
	The threshold of 3% appears to be an arbitrary level.  This level may be rooted in Operational and Planning studies that consider impacts from outages on one TP's system that increase loading on an element of another TP's system by 3% or more.  While this level may be a good indicator of impact, it may not provide an indicator of which party's ownership or allocation of facilities is being used.  It does not assure TPs will be able to preserve their rights (i.e. by contractual allocation) with a fixed threshold of 3%

	Response: SDT needs to review and respond.

	Entergy
	
	(
	The threshold level of 3% for third party should not be included in this standard since there is no such threshold level for Transmission Service Provider's own data.

	Response: SDT needs to review and respond.

	ERCOT
	
	(
	See IRC comments submitted by Charles Yeung.

	Response: See response to IRC comments submitted by Charles Yeung.

	FirstEnergy
	(
	
	

	IESO
	
	(
	We assume the third party is a 1 tier or 2 tier Control Area adjacent to the Tariff footprint of the TSP.  Some questions:

• Paragraph talks about impact transmission capability with 3%. Does this mean impact any flow gate within the Tariff footprint of the TSP with 3%. What about flow gates that are tie lines between Tariff footprint and 1tier and limiting element is in 1tier.  

• What participation factors and generators should be used to determine if  the GLDF of commonly dispatched units of 1tier Control Area  is >3%.  NERC IDC? 

• Is the data listed in bullet point 2,3,4,5,6 of R16 going to be submitted by neighbor TSP. If so it is sufficient to specify that a TSP is getting the list of Reservations as specified in 2,3,4,5,6 of R16 from a neighboring TSP without having to know detail as specified in the bullet points.

	Response: SDT needs to review and respond.

	IRC
	
	(
	We assume third party is a 1 tier or 2 tier Control Area adjacent to the Tariff footprint of the TSP.   Some questions:

•  Paragraph talks about impact transmission capability with 3%. Does this mean impact any flow gate within the Tariff footprint of the TSP with 3%. What about flow gates that are tie lines between Tariff footprint and 1tier and limiting element is in 1tier.  

•  What participation factors and generators should be used to determine if  the GLDF of commonly dispatched units of 1tier Control Area  is >3%.  NERC IDC? 

•  Is the data listed in bullet point 2,3,4,5,6 of R16 going to be submitted by neighbor TSP. If so it is sufficient to specify that a TSP is getting the list of Reservations as specified in 2,3,4,5,6 of R16 from a neighboring TSP without having to know detail as specified in the bullet points.

	Response: SDT needs to review and respond.

	ITC
	(
	
	This is overdue in our estimation.  Using 5%, as some have done, has resulted in unnecessary TLRs, particularly on lower voltage (138kV and below) systems.

	Response: 5% is as arbitrary as 3%.  For consistency, TSP should be required to use the same threshold as it uses impact of its own reservations. 

	MEC Trading
	
	(
	If is this appropriate for MOD-30, it is appropriate for MOD-28.  Why do you specifically spell out a requirement for MOD-30 but not MOD-28?

	Response: SDT will make appropriate adjustment to MOD-028.

	MEC
	
	(
	The impacts by more than 3% are consistent with post-contingent flowgates.  It should be noted that pre-contingent flowgates are continuing to exist in the area.  Such pre-contingent flowgates have physical conditions that would be improperly represented by post-contingent flowgates so the pre-contingent flowgates must remain in place.  The pre-contingent flowgates in the area generally only consider significant those third-party impacts that are at 5% or more.  Therefore, provisions should be made in R16 to allow the appropriate screen, 3% or 5%, for the appropriate type of flowgate, post-contingent or pre-contingent.

	Response: SDT needs to review and respond.

	Manitoba Hydro
	
	(
	During a TLR or redispatch, a 3% cutoff would require the third party to adjust their resources by up to 33 MW for every 1MW of relief.  I believe that this is too much. I would recommend third party mitigation has to be a balance of impact and ability for relief and those 3% biases that balance.  I would recommend that the 5% impact which still requires a potential 20 MW adjustment for every 1 MW of relief maintains the balance between impact and ability for relief.

	Response: SDT needs to review and respond.

	MRO
	
	(
	The impacts by more than 3% are consistent with post-contingent flowgates.  It should be noted that pre-contingent flowgates are continuing to exist in the MRO area.  Such pre-contingent flowgates have physical conditions that would be improperly represented by post-contingent flowgates so the pre-contingent flowgates must remain in place.  The pre-contingent flowgates in the MRO generally only consider significant those third-party impacts that are at 5% or more.  Therefore, provisions should be made in R16 to allow the appropriate screen, 3% or 5%, for the appropriate type of flowgate, post-contingent or pre-contingent.

	Response: SDT needs to review and respond.

	PSC SC
	(
	
	


9. Are you aware of any conflicts between the proposed standard and any regulatory function, rule/order, tariff, rate schedule, legislative requirement or agreement?  If “Yes,” please the conflict in the comments area. 


Summary Consideration:  

	Question #9

	Commenter
	Yes
	No
	Comment

	SMUD
	
	(
	

	Entergy
	
	(
	

	ERCOT
	(
	
	ERCOT is a separate Interconnection and Region connected to the Eastern Interconnection through DC ties.  Texas Senate Bill 7 effective on 9/1/99 amended the Texas utilities code to provide for the restructuring of the electric utility industry within the ERCOT Interconnection. The act deregulated the electricity generation market to allow for competition in the retail sale of electricity. As of July 2001 the ERCOT interconnection began operation as a single Balancing Authority Interconnection and implemented a market in accordance with the Texas Public Utility commission ruling. Since the implementation of this Act, all of ERCOT has been a single Balancing Authority Area and there has been no reservation of transmission capacity in ERCOT.

Available Transfer Capability is defined as the measure of the transfer capability remaining in the physical transmission network for further commercial activity over and above already committed uses. It is defined as Total Transfer Capability less existing transmission commitments (including retail customer service), less a Capacity Benefit Margin, less a Transmission Reliability Margin. The ERCOT Interconnection has already moved “beyond” ATC and into a Market design which  resulted in the disappearance of an explicit transmission service product. In addition the DC Tie transfer capability is planned and coordinated by a TSP  that is a member of both Regions and therfore both ERCOT and SPP are notified when the DC Tie capability is reduced. 

Under ERCOT market rules, Transmission Service allows all eligible transmission service customers to deliver energy from resources to serve load obligations, using the transmission facilities of all of the Transmission Service Providers in ERCOT. Currently ERCOT employs a zonal congestion management scheme that is flow-based, whereby the ERCOT transmission grid, including attached generation resources and load, are divided into a predetermined number of congestion zones. This congestion management scheme applies zonal shift factors, determined by ERCOT, to predict potential congestion under the known topology of the ERCOT System. This scheme is used in the Day Ahead and Adjustment Periods to evaluate potential congestion. During the operating period ERCOT uses zonal shift factors to determine zonal Redispatch deployments needed to maintain flows within zonal limits. The local congestion management scheme relies on a more detailed Operational Model to determine how each particular Resource or Load impacts the transmission system.  This model uses the current known topology of the transmission system. Unit specific Redispatch instructions are then issued to manage local congestion. 

In the future ERCOT will be transitioning from a Zonal Market to a full LMP market.  This system is designed to manage congestion in the Day Ahead and Real-Time on a Resource specific basis. Under both of these market designs transmission facility limits are established in advance and updated based on coordinated exchange of information between transmission providers and ERCOT in planning and operating periods.

 In the current and future ERCOT market design the method of calculating ATC, TTC and the use of CBM and TRM are not applicable to the ERCOT Region. ERCOT does not have a synchronous connection with any other Balancing Authority Area, and does not use the transmission reservation and scheduling practices addressed by these standards. ERCOT requests the drafting team consider revising the wording so that Responsible Entitles required to conform to the standards are those that are synchronously connected with other Control Areas and/or offer transmission reservations and schedules within the interconnection. We also recommend that the standard allow for ERCOT exception or exemption from calculation and posting of ATC, TTC, CBM, and TRM without the need for a Regional variance.  

	Response:  SDT needs to review and respond.

	FirstEnergy
	
	(
	

	ITC
	
	(
	There are 3 methods, pick the one that works.  We have noted in our other comments that some entities, such as New England, have approved tariffs that don't require the sale of transmission service.  They should not have to pick any method but should, as we have noted, be required to provide data to neighboring TSPs that do sell transmission service.

	Response: If there is a Transmission Service Provider, it has to calculate and post ATCs.

	MEC Trading
	(
	
	This standard is not requiring consistenecy per the requirement of FERC Order 890.

	Response: SDT does not interpret consistency to mean only one method for ATC calculations.

	MEC
	
	(
	

	Manitoba Hydro
	
	(
	

	MRO
	
	(
	

	PSC SC
	
	(
	


10. Please provide any other comments (that you have not already provided in response to the questions above) that you have on the draft standard MOD-030-1. 

Summary Consideration:  

	Question #10

	Commenter
	Yes
	No
	Comment

	SMUD
	
	
	A. R1.2 should be modified due to the fact that Facilities don't cause congestion, rather they    experience congestion.  The following change to the language would be more accurate:

"How the methodology identifies transmisison Facilities that are expected by the AFC calculator to experience congestion on the transmission system."

B. See comments on MOD-29.

In the "Applicability" section, the term "Available Transfer Capability Implementation Document" is used as a defined term.  The term is used in MOD-01 R3.  At minimum the ATCID either needs to be defined or a reference to the MOD-01 must be inserted for cross reference.

C. R.1 through R.3. appear to be a prohibited "fill-in-the-blank."

D. R22.  Typo.  Change "covert" to "convert."



	Response: SDT agrees to clarify the language in R1.2 to reflect that facilities experience congestion rather than causing congestion.  ATCID is defined in R1.  R1 through R3 are fill-in-the-blank type of requirements that are included for transparency purposes.  R22 shall be changed to correct the typo.

	BPA
	
	
	The ATC MOD’s (MOD-001-1, MOD-028-1, MOD-029-1, and MOD-030-1) do not clearly distinguish the methodologies and their applications.  Please provide descriptions of these methodologies.

The Applicability section 4.1. through 4.3. Should have the phrase "Available Transfer Capabilities for paths" replaced with "Available Flowgates Capabilities for Flowgates".

R1.2. should be modified due to the fact that Facilities don't cause congestion, rather they experience congestion.  The following change to the language would be more accurate:

"How the methodology identifies transmisison Facilities that are expected by the AFC calculator to experience congestion on the transmission system."

R3.   A Flowgate should not be defined as a thermal, voltage, or stability type due to the fact that Flowgates are limited by thermal, voltage, or stability problems that can vary depending on system conditions.

R4. through R8. should be combined into two requirements:

1) Each entity generating Flowgate limit values (note that it's not clear if this should be the Transmission Owner, Transmission Planner, Planning Coordinator, and/or Reliability Coordinator) shall provide current Flowgate limit data to Transmission Service Providers (TSPs); and

2) TSPs shall use the lesser of the thermal, voltage, or stability limits that apply to the current system conditions.

R18.-sub-bullet 5, R23., and R24. should each have the "ATC"s replaced with "AFC"s, for the reasons explained in our response to the MOD-030-1 Comment Form's question 4.

R24. should have "path" replaced with "Flowgate", for the reasons explained in our response to the MOD-030-1 Comment Form's question 4.

	Response: SDT agrees with the comment about more clearly distinguishing three methodologies.  ATCs are ultimately required to be calculated on paths, therefore, the language in Applicability Section 4.1 through 4.3 is correct.  R1.2 shall modified as suggested.  R3 - For transparency purposes, the TSP is required to identify if the flowgate is limited by the thermal, stability or voltage considerations. R4 – R8 – SDT shall consider combining these requirements as suggested.  SDT shall review Comments regarding R24 sub-bullets to replace ATC to AFC.  R23 and R24 correctly include ATC as these need to accommodate un-scheduled non-firm reservations and posting of ATCs.  There is no requirements to post AFC values on OASIS.  The requirement is to post ATC values for posted paths after converting them from AFC values.  R24 is referring to path correctly and should not be referring to Flowgate”.

	Duke
	
	
	R1.1 does not create the same level of transmission service as created in MOD-028.  MOD 028 R6.1 involves N-1 transmission contingency AND ramping/partial contingency of generation.  MOD-030 R1.1 appears to only require N-1 transmission or generation contingency.  This is not comparable service.

For R3. need to also include why the Flowgate is a limit

	Response: SDT agrees with the commenter, there can not be one size fits all so some difference will exist due to use of different ATC methodologies.  By including the reason thermal, stability, or voltage for the limit, it is implied that why flowgate is a limit.  

	ITC
	
	
	We think this is a much better standard than MOD-028 and -029.  It should provide for greater flexibility and reliability.  We think all methods should be examined closely if there is any evidence of overselling (as evidenced byTLRs and market congestion) or underselling (as evidenced by denial of service without TLRs or market congestion).

	Response: SDT should consider and respond to this comment.

	MEC Trading
	
	
	This MOD should be combined with MOD-28 and everyone using a distribution factor based analysis should use the same methodology and the amount of consistency should be increased significantly.

	Response: SDT should consider and respond to this comment.

	MEC
	
	
	1.  R1.1 implies that the only planning criteria that should be used in ATC calculations is Category B in Table 1 of the NERC Standards.  That is incorrect, the methodology should describe how it meets the planning criteria that is appropriate for posted values including  applicable NERC Standards, regional criteria, Transmission Owner criteria, etc.  Therefore, R1.1 should state that "How methodology meets the planning criteria in NERC Standards, regional standards, Transmission Owner's planning criteria, Transmission Planner's planning criteria, and other applicable planning criteria used by the Transmission Planner to plan the system.  2.  R8 does not cover all the limitations that are possible for flowgates, for example, the limitation may be due to high transfers causing low voltage on the system after the next condition.  This is not an example of a thermal rating or a voltage limit of the power transfer.  I suggest that an additional bullet be added to R8 stating "Any other constraint to power transferred across the Flowgate, if applicable.  For such constraints, the constraint should be defined, explained, and examples given in the methodology so as to ensure that the ATC methodology is transparent."   As an alternative, a bullet should be added for "Steady-state voltage constraint."  3.  The scheduling time horizon should be clarified. 4.  The Standards Drafting Team indicated that they have decided not to define the term Existing Transmission Commitments, yet R13 uses that defined term with capital letters.  The words Existing Transmission Commitments in R13 and elsewhere in the standard should not be capitalized so as not to indicate a defined term.  5.  R22 change "covert" to "convert".

	Response: R1.1 SDT should consider and respond to this comment. R8. SDT agrees with the comment and will modify the standard to include other constraints.  Scheduling time horizon and other horizons shall be clarified.  R13 - ETC is proposed to be defined.  R22 – SDT shall modify the standard to reflect correction of the typo.

	MRO
	
	
	1.  R1.1 implies that the only planning criteria that should be used in ATC calculations is Category B in Table 1 of the NERC Standards.  That is incorrect, the methodology should describe how it meets the planning criteria that is appropriate for posted values including  applicable NERC Standards, regional criteria, Transmission Owner criteria, etc.  Therefore, R1.1 should state that "How methodology meets the planning criteria in NERC Standards, regional standards, Transmission Owner's planning criteria, Transmission Planner's planning criteria, and other applicable planning criteria used by the Transmission Planner to plan the system.  2.  R8 does not cover all the limitations that are possible for flowgates, for example, the limitation may be due to high transfers causing low voltage on the system after the next condition.  This is not an example of a thermal rating or a voltage limit of the power transfer.  The MRO suggests that an additional bullet be added to R8 stating "Any other constraint to power transferred across the Flowgate, if applicable.  For such constraints, the constraint should be defined, explained, and examples given in the methodology so as to ensure that the ATC methodology is transparent."   As an alternative, the MRO recommends that a bullet be added for "Steady-state voltage constraint."  3.  MRO believes the scheduling time horizon should be clarified. 4.  The Standards Drafting Team indicated that they have decided not to define the term Existing Transmission Commitments, yet R13 uses that defined term with capital letters.  The words Existing Transmission Commitments in R13 and elsewhere in the standard should not be capitalized so as not to indicate a defined term.  5.  R22 change "covert" to "convert".

	Response: R1.1 SDT should consider and respond to this comment. R8. SDT agrees with the comment and will modify the standard to include other constraints.  Scheduling time horizon and other horizons shall be clarified.  R13 - ETC is proposed to be defined.  R22 – SDT shall modify the standard to reflect correction of the typo.

	SERC ATCWG 
	
	
	The updating of flowgates as specified in Requirement 2 should be annually rather than quarterly.

	Response: SDT should consider and respond to this comment.

	SRP
	
	
	The standard should describe how flowgates and reliability limits should be determined such as is done for the Network Response Methodology MOD028 in requirement R6 and is done for the Rated System Path Methodology MOD029 in requirement R6.
Requirements R1.1, R1.2 & R1.3 are fill-in-the-blank requirements and need to specify rather than ask the tsp to explain what they do.

R8 - The standard should specify how the thermal, voltage and stability limited are determined.  For example, are these n-0 or n-1 limits and are they transient or post-transient?



	Response: SDT should consider and response to this comment.  However, R8 describes how flowgate TFC should be calculated.  There does not appear to be a need to be more descriptive requirement as it is not a facility rating standard. SDT agrees that R1.1, R1.2 and R1.3 are fill in the blank requirements included for transparency. 


� The appeals process is in the Reliability Standards Development Procedures: http://www.nerc.com/standards/newstandardsprocess.html.  








Page 30 of 30

