Transmission Loading Relief Standard – Version 0, Draft 2


Interchange Distribution Calculator (IDC) Reference Documentation
Introduction

The Interchange Distribution Calculator (IDC) Reference Documentation documents the implementation of the NAESB business practices and the NERC reliability standards associated with the Eastern Interconnection Transmission Loading Relief (TLR) congestion management process.  The IDC Reference Documentation explains how the IDC manages the interchange transaction reallocation process, and provides several examples of the timing associated with interchange transaction curtailments under various TLR levels.
Index

1. Section A: How the IDC Handles Reallocation

2. Section B: Communication and Timing Requirements to Support Reallocation
3. Section C: IDC Features that Support Transaction Reloading/Reallocation

a. Information posted from IDC to NERC TLR site.

b. IDC Logic, IDC Report, and Timing

c. Reloading/Reallocation Transaction Status

d. Reallocation/Reloading Priorities 

e. Total Flow Value on a Constrained Facility for Next Hour 

4. Section D: Timing Requirements

a. TLR Levels 3a and 5a Issuing/Processing Time Requirement

b. Re-Issuing of a TLR Level 2 or Higher

c. IDC Assistance with Next Hour Point-to--Point Transactions

d. IDC Calculations and Reporting 

e. Assignment of Interchange Transaction Status

f. Tag Reloading for TLR Levels 1 and 0

g. New Tag Alarming

h. Tag Adjustment

i. Special Tag Status

j. Transaction Sub-Priority Examples

5. Section E: Interchange Transaction Curtailments During TLR Level 3b
6. Section F: Considerations for Interchange Transactions Using Firm Point-to-Point Transmission Service
7. Section G: IDC Treatment of TLR Level 6

Section A: How the IDC Handles Reallocation
The IDC algorithms reflect the reallocation and reloading principles presented in this Reference Documentation, as well as the reporting requirements, and status display.  The IDC will obtain the tag submittal time from the tag authority, and post the reloading/reallocation information to the NERC TLR site.  

Section C (IDC Features that Support Transaction Reloading/Reallocation) provides a summary of IDC features that support the reallocation process, and Section D (Timing Requirements) provides the details on the interface and display features.  Refer to Version 1.7.095 NERC Transaction Information Systems Working Group  (TISWG) Electronic Tagging Functional Specification for details about the E-Tag system.
Section B: Communication and Timing Requirements to Support Reallocation
This section covers the communication and timing requirements to support reallocation during TLR Levels 3a and 5a.  It should be noted that calling a TLR 3a does not necessarily mean that Interchange Transactions using Non-firm Transmission Service will always be curtailed the next hour.  However, TLR Levels 3a and 5a trigger the approved tag submission deadline for Reallocation requirements and allow for a coordinated assessment of all Interchange Transactions tagged to start the upcoming hour. 
The following timeline shall be utilized to support reallocation decisions during TLR Levels 3a or 5a. See Figures 2 and 3 for a depiction of the reallocation time line.

1. [image: image3.emf]00:00

Beginning of

Current Hour

01:00 02:00

Beginning of

Next Hour

00:25

Approved-Tag

Submission

Deadline for

Reallocation at 01:00

Approved-Tag

Submission

Deadline for

Reallocation at 02:00

01:25

Time Convention. In this section, the beginning of the current hour shall be referenced as 00:00.  The beginning of the next hour shall be referenced as 01:00.  The end of the next hour shall be referenced as 02:00. See Figure 1.

2. [image: image4.wmf]MW

Time

10

20

40

S1

TLR

Approved tag submission deadline for reallocation.  The reliability coordinators shall consider all approved tags for interchange transactions at or above the curtailment threshold that have been submitted to the IDC by 00:25 for reallocation at 01:00. See Figure 1.  However, interchange transactions using firm point-to-point transmission service will be allowed to start as scheduled.

a. Reliability coordinators shall consider all approved tags submitted to the IDC beyond these deadlines for reallocation at 02:00 (for both firm and non-firm point-to-point transmission service).  However, these interchange transactions will not be allowed to start or increase at 01:00. 

b. The approved tag submission deadline for reallocation shall cease to be in effect as soon as the TLR level is reduced to 1 or 0.

3. Off-hour Transactions. Interchange transactions with a start time other than xx:00 shall be considered for reallocation at xx+1:00.  For example, an interchange transaction with a start time of 01:05 and whose tag was submitted at 00:15 will be considered for reallocation at 02:00.

4. Tag Evaluation Period.  Balancing authorities and transmission providers shall evaluate all tags submitted for reallocation and shall communicate approval or rejection by 00:25.

[image: image1.emf]00:00 01:00 00:20 00:10 00:30 00:40 00:50

00:25

Beginning of

Current Hour

Approved-Tag

Submission

Deadline for

Reallocation

(Must be in IDC for

Realloction at 01:00)

RC Sends Reallocation

notifications. BAs

curtail Non-firm

Transactions

and notify PSEs

TLR 3a

Firm Transactions

that are in IDC by

00:25 or by the

time the TLR is

declared (if later)

start as scheduled

TLR Re-issue

Alarm

Congestion

Management

Report to Issuing

Reliability Coordinator

Congestion Management

Report confirmed by Issuing

Reliability Coordinator

Congestion

Management

Report confirm by

Reliability Coordinator of

Sink Balancing Area

00:35

Adjust Lists sent to LBAs,

GBAs, authoring PSEs

00:45

Adjust

Tables from

LBAs

Potential Adjust List

Issued

Reallocation begins for Non-

firm Transactions that are in

IDC by 00:25 and for Firm

Transactions that are in by

the time the TLR is declared if

it is declared after 00:25.

Others are held for

Reallocation at 02:00.

00:00 01:00 00:20 00:10 00:30 00:40 00:50

00:25

Beginning of

Current Hour

Approved-Tag

Submission

Deadline for

Reallocation

(Must be in IDC for

Realloction at 01:00)

RC Sends Reallocation

notifications. BAs

curtail Non-firm

Transactions

and notify PSEs

TLR 3a

Firm Transactions

that are in IDC by

00:25 or by the

time the TLR is

declared (if later)

start as scheduled

TLR Re-issue

Alarm

Congestion

Management

Report to Issuing

Reliability Coordinator

Congestion Management

Report confirmed by Issuing

Reliability Coordinator

Congestion

Management

Report confirm by

Reliability Coordinator of

Sink Balancing Area

00:35

Adjust Lists sent to LBAs,

GBAs, authoring PSEs

00:45

Adjust

Tables from

LBAs

Potential Adjust List

Issued

Reallocation begins for Non-

firm Transactions that are in

IDC by 00:25 and for Firm

Transactions that are in by

the time the TLR is declared if

it is declared after 00:25.

Others are held for

Reallocation at 02:00.


Figure 2 — Reallocation Timing for TLR 3a Called at 00:08

5. Collective Scheduling Assessment Period. At 00:25, the initiating reliability coordinator (the one who called and still has a TLR 3a or 5a in effect) shall run the IDC to obtain a three-part list of interchange transactions including their transaction status: 

a. Interchange transactions that may start, increase, or reload shall have a status of PROCEED, and 

b. Interchange transactions that must be curtailed or interchange transactions whose tags were submitted prior to the TLR 2 or higher being declared but were not permitted to start or increase shall have a status of CURTAILED, and 

c. Interchange transactions that are entered into the IDC after 00:25 shall have a status of HOLD and be considered for reallocation at 02:00.  Also, interchange transactions using non-firm point-to-point transmission service submitted after TLR 2 or higher was declared (“post-tagged”) but have not been allowed to start shall retain the HOLD status until given permission to PROCEED or e-tag expires. (Note: TLR Level 2 does not hold interchange transactions using firm point-to-point transmission service).
[image: image2.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Approved-Tag

Submission

Deadline for

Reallocation

(Must be in IDC for

Reallocation at 01:00)

RC Sends Reallocation

notifications. BAs

implement reductions of Firm

Transactions on pro-rata basis

and notify PSEs

Firm Transactions

that are in IDC by

time TLR is

declared or 00:25,

whichever is later,

start as scheduled

TLR 5a

Reallocation begins for Firm

Transactions that are in IDC

by time TLR is declared or

00:25, whichever is later.

Others are held for

Reallocation at 02:00

00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Approved-Tag

Submission

Deadline for

Reallocation

(Must be in IDC for

Reallocation at 01:00)

RC Sends Reallocation

notifications. BAs

implement reductions of Firm

Transactions on pro-rata basis

and notify PSEs

Firm Transactions

that are in IDC by

time TLR is

declared or 00:25,

whichever is later,

start as scheduled

TLR 5a

Reallocation begins for Firm

Transactions that are in IDC

by time TLR is declared or

00:25, whichever is later.

Others are held for

Reallocation at 02:00


Figure 3 — Reallocation timing for TLR 5a called at 00:08.

d. The initiating reliability coordinator shall communicate the list of interchange transactions to the appropriate sink reliability coordinators via the IDC, who shall in turn communicate the list to the sink balancing authorities at 00:30 for appropriate actions to implement interchange transactions (CURTAIL, PROCEED or HOLD).  The IDC will prompt the initiating reliability coordinator to input the necessary information (i.e., maximum flowgate loading and curtailment requirement) into the IDC by 00:25. 

e. Subsequent required reports before 01:00 shall allow the reliability coordinators to include those interchange transactions whose tags were submitted to the IDC after the approved tag submission time for reallocation and were given the HOLD status (not permitted to PROCEED).  Transactions at or above the curtailment threshold that are not indicated as PROCEED on reload/reallocation report shall not be permitted to start or increase the next hour.

Discussion: Note that TLR 2 does not initiate the approved tag submission deadline for reallocation, but a TLR3a or 5a does.  It is, however, important to recognize the time when a TLR 2 is called, where applicable, to determine the status of a held transaction – “CURTAILED” if tagged before the TLR was called but “HOLD” if tagged after the TLR was called.

f. In running the IDC, the reliability coordinator shall have an option to specify the maximum loading of the constrained facility by all interchange transactions using point-to-point transmission service.

Discussion: This allows the reliability coordinator to take into consideration SOLs or IROLs and changes in interchange transactions using other than point-to-point transmission service taken under the open access transmission tariff.  This option is needed to avoid loading the constrained facility to its limit with known interchange transactions while other factors push the facility into a SOL or IROL violation and hence triggering the declaration of a TLR 3b or 5b.

g. Notification of interchange transaction status shall be provided from the IDC to the reliability coordinators via an IDC report.  The reliability coordinators shall communicate this information to the balancing authorities and transmission operators. 

6. Customer Preferences on Timing to Call TLR 3a or 5a. Reliability coordinators shall leave a TLR 2 and call a TLR 3a as soon as possible (but no later than 30 minutes) to initiate the approved tag submission deadline and start reallocating interchange transactions.  Nevertheless, recognizing the approved tag submission deadline for reallocation, from a transmission customer perspective, it is preferable that the reliability coordinator calls a TLR 3a within a certain time period to allow for tag preparation and submission.  See Figure 4.

Discussion: A reliability coordinator calls a TLR 2 or 3a whenever it deems necessary to indicate that a transmission facility is approaching its SOL or IROL.  It is envisioned, though not required, that a TLR 2 or 3a is preceded by a period of a TLR 1 declaration, hence transmission customers should normally have advance notice of a potential constraint.  For example, a TLR 3a initiated during the period 01:00 to 01:25 would allow the purchasing-selling entity to submit a tag for entry into the IDC by the approved tag submission deadline for reallocation at 02:00.  See Figure 4.  However, the preferred time period to declare a TLR 3a or 5a would be between 00:40 (when tags for next hour market have been submitted) and 01:15.  This will allow the transmission customers a range of 15 to 35 minutes to prepare and submit tags.  (Note: In this situation, the reliability coordinator would need to reissue the TLR 3a at 01:00.)

It must be emphasized that the preferred time period is not a requirement, and should not in any way impede a reliability coordinator’s ability to declare a TLR 3a, 3b, 4, 5a, or 5b whenever the need arises.

[image: image5.wmf]MW

Time

10

20

40

S3

S1

TLR


Figure 4. “Ideal" time for issuing TLR 3a for Reallocation at 02:00.

Section C: IDC Features that Support Transaction Reloading/Reallocation

Following is a summary of IDC features and E-Tag interface that support reloading/reallocation: 

Information posted from IDC to NERC TLR site.

1. Restricted directions (all source/sink combinations that impact a constrained facility(ies) with TLR 2 or higher) will be posted to the NERC TLR site and updated as necessary. 

2. TLR constrained facility status and transfer distribution factors (TDFs) will continue to be posted to NERC TLR site. 

3. Lowest priority of interchange transactions (marginal “bucket”) to be reloaded/reallocated next-hour on each TLR constrained facility will be posted on NERC TLR site. This will provide an indication to the market of priority of interchange transactions that may be reloaded/reallocated the following hours. 

IDC Logic, IDC Report, and Timing

1. The reliability coordinator will run the IDC the reloading/reallocation report at approximately 00:26.  The IDC will prompt the reliability coordinator to enter a maximum loading value.  The IDC will alarm if the reliability coordinator doesn’t enter this value and issue a report by 00:30 or change from TLR 3a Level.  The report will be distributed to balancing authorities and transmission operators at 00:30.  This process repeats every hour as long as the approved tag submission deadline for reallocation is in effect (or until the TLR level is reduced to 1 or 0).

2. For interchange transactions in the restricted directions, tags must be submitted to the IDC by the approved tag submission deadline for reallocation to be considered for reallocation next-hour.  The time stamp by the tag authority is regarded the official tag submission time.

3. Tags submitted to IDC after the approved tag submission deadline for reallocation will not be allowed to start or increase but will be considered for reallocation the next hour. 

4. Interchange transactions in restricted directions that are not indicated as “PROCEED” on the reload/reallocation report will not be permitted to start or increase next hour.

Reloading/Reallocation Transaction Status

Reloading/Reallocation status will be determined by the IDC for all interchange transactions. The reloading/reallocation status of each interchange transaction will be listed on IDC reports and NERC TLR site as appropriate. An interchange transaction is considered to be in a restricted direction if it is at or above the curtailment threshold. Interchange transactions below the curtailment threshold are unrestricted and free to flow subject to all applicable reliability standards, business practices, and transmission tariff rules. 

1. HOLD.  Permission has not been given for the interchange transaction to start or increase, and it is waiting for the next reloading/reallocation evaluation for which it is a candidate.  Interchange transactions with E-tags submitted to the tag authority prior to TLR 2 or higher being declared (pre-tagged) will change to CURTAILED Status upon evaluation that does not permit them to start or increase.  Interchange transactions, with E-tags submitted to the tag authority after TLR 2 or higher was declared (post-tagged), will retain HOLD Status until given permission to proceed or the E-Tag expires.

2. CURTAILED.  Interchange transactions for which E-Tags were submitted to tag authority prior to TLR 2 or higher being declared (pre-tagged) and ordered to be curtailed totally, curtailed partially, not permitted to start, or not permitted to increase.  Interchange transactions (pre-tagged or post-tagged) that were flowing and ordered to be reduced or totally curtailed. The balancing authority will indicate to the IDC through the E-Tag adjustment table the interchange transaction’s curtailed values.

3. PROCEED:  Interchange transaction is flowing or has been permitted to flow as a result of Reloading/Reallocation evaluation. The balancing authority will indicate through the E-Tag adjustment table to IDC if the interchange transaction will reload, start, or increase next-hour per PSE’s energy schedule as appropriate.

Reallocation/Reloading Priorities 

1. Interchange transaction candidates are ranked for loading and curtailment by priority.  This is called the “Constrained Path Method,” or CPM. (secondary, hourly, daily, … firm etc).  Interchange transactions are curtailed and loaded pro-rata within priority level per TLR algorithm.

2. Reloading/Reallocation of interchange transactions are prioritized first by priority per CPM.  E-Tags must be submitted to the IDC by the approved tag submission deadline for reallocation of the hour during which the interchange transaction is scheduled to start or increase to be considered for reallocation. 

3. During reloading/reallocation, interchange transactions using lower priority transmission service will be curtailed pro-rata to allow higher priority transactions to reload, increase, or start. Equal priority interchange transactions will not reload, start, or increase by pro-rata curtailment of other equal priority interchange transactions. 

4. Reloading of interchange transactions using non-firm transmission service with CURTAILED Status will take precedence over starting or increasing of interchange transactions using non-firm transmission service of the same priority with PENDING Status. 

5. Interchange transactions using firm point-to-point transmission service will be allowed to start as scheduled under TLR 3a as long as their E-Tag was received by the IDC by the approved tag submission deadline for reallocation of the hour during which the interchange transaction is due to start or increase, regardless of whether the E-tag was submitted to the tag authority prior to TLR 2 or higher being declared or not.  If this is the initial issuance of the TLR 3a, interchange transactions using firm point-to-point transmission service will be allowed to start as scheduled as long as their E-Tag was received by the IDC by the time the TLR is declared.
Total Flow Value on a Constrained Facility for Next Hour 

1. The reliability coordinator will calculate the change in net flow on a constrained facility due to reallocation for the next hour based on:

1.1. Present constrained facility loading, present level of interchange transactions, and balancing authorities NNL responsibility (TLR Level 5a) impacting the constrained facility,

1.2. SOLs or IROLs, known interchange impacts and balancing authority NNL responsibility (TLR Level 5a) on the constrained facility the next hour, and

1.3. Interchange transactions scheduled to begin the next hour.

2. The reliability coordinator will enter a maximum loading value for the constrained facility into the IDC as part of issuing the reloading/reallocation report.

3. The reliability coordinator is allowed to call for TLR 3a or 5a when approaching a SOL or IROL to allow maximum transactional flow next hour, and to manage flows without violating transmission limits.

4. The simultaneous curtailment and reallocation for a constrained facility is allowed. This reduces the flow over the constrained facility while allowing interchange transactions using higher priority transmission service to start or increase the next hour. This may be used to accommodate change in flow next-hour due to changes other than point-to-point interchange transactions while respecting the priorities of interchange transactions flowing and scheduled to flow the next hour. The intent is to reduce the need for using TLR 3b, which prevents new interchange transactions from starting or increasing the next hour. 

5. The reliability coordinator must allow interchange transactions to be reloaded as soon as possible.  Reloading must be in an orderly fashion to prevent a SOL or IROL violation from (re)occurring and requiring holding or curtailments in the restricted direction.

Section D: Timing Requirements

TLR Levels 3a and 5a Issuing/Processing Time Requirement

1. [image: image6.wmf]MW

Time

10

20

40

S2

S1

TLR

In order for the IDC to be reasonably certain that a TLR Level 3a or 5a re-allocation/reloading report in which all tags submitted by the approved-Tag submission deadline for reallocation are included, the report must be generated no earlier than 00:25 to allow the 10-minute approval time for interchange transactions that start next hour. 

2. [image: image7.wmf]MW

TLR

Time

10

20

40

S3

S2

S1

In order to allow a reliability coordinator to declare a TLR Level 3a or 5a any time during the hour, the TLR declaration and reallocation/reloading report distribution will be treated as independent processes by IDC.  That is, a reliability coordinator may declare a TLR Level 3a or 5a at any time during the course of an hour.  However, if a TLR Level 3a or 5a is declared for the next hour prior to 00:25 (see Figure 5 at right), the reallocation/reloading report that is generated will be made available to the issuing reliability coordinator only for previewing purposes, and can not be distributed to the other reliability coordinators or the market.  Instead, the issuing reliability coordinator will be reminded by an IDC alarm at 00:25 to generate a new reallocation/reloading report that will include all tags submitted prior to the approved tag submission deadline for reallocation. 

3. A TLR Level 3a or 5a reallocation/reloading report must be confirmed by the issuing reliability coordinator prior to 00:30 in order to provide a minimum of 30 minutes for the reliability coordinators with tags sinking in its reliability area to coordinate the reallocation and reloading with the sink balancing authorities. This provides only 5 minutes (from 00:25 to 00:30) for the issuing reliability coordinator to generate a reallocation/reloading report, review it, and approve it.

4. The TLR declaration time will be recorded in the IDC for evaluating transaction sub-priorities for reallocation/reloading purposes (see Sub-priority Table, in the IDC Calculations and Reporting section below).

Re-Issuing of a TLR Level 2 or Higher

Each hour, the IDC will automatically remind the issuing reliability coordinator (via an IDC alarm) of a TLR level 2 or higher declared in the previous hour or earlier about re-issuing the TLR. The purpose of the reminder is to enable the reliability coordinator to reallocate or reload currently halted or curtailed interchange transactions next hour. The reminder will be in the form of an alarm to the issuing reliability coordinator, and will take place at 00:25 so that, if the reliability coordinator re-issues the TLR as a TLR level 3a or 5a, all tags submitted prior to the approved tag submission deadline for reallocation are available in the IDC. 

IDC Assistance with Next Hour Point-to--Point Transactions

In order to assist a reliability coordinator in determining the MW relief required on a constrained facility for the next hour for a TLR level 3a or 5a, the IDC will calculate and present the total MW impact of all currently flowing and scheduled point-to-point interchange transactions for the next hour.  In order to assist a reliability coordinator in determining the MW relief required on a constrained facility for the next hour during a TLR level 5a, the IDC will calculate and present the total MW impact of all currently flowing and scheduled point-to-point interchange transactions for the next hour as well as balancing authorities with flows due to service to network customers and native load.  The reliability coordinator will then be requested to provide the total incremental or decremental MW amount of flow through the constrained facility that can be allowed for the next hour.  The value entered by the reliability coordinator and the IDC-calculated amounts will be used by the IDC to identify the relief/reloading amounts (delta incremental flow value) on the constrained facility.  The IDC will determine the interchange transactions to be reloaded, reallocated, or curtailed to make room for the interchange transactions using higher priority transmission service. The following examples show the calculation performed by IDC to identify the delta incremental flow:

Example 1

	Flow to maintain on constrained facility
	800 MW

	Expected flow next hour from interchange transactions using point-to-point transmission service
	950 MW

	Contribution to flow next hour from service to network customers and native load
	-100 MW

	Expected net flow next hour on constrained facility
	850 MW

	Amount of interchange transactions using point-to-point transmission service to hold for reallocation
	850 MW – 800 MW = 50 MW

	Amount to enter into IDC for interchange transactions using point-to-point transmission service
	950 MW – 50 MW = 900 MW


Example 2

	Flow to maintain on constrained facility
	800 MW

	Expected flow next hour from interchange transactions using point-to-point transmission service
	950 MW

	Contribution to flow next hour from service to network customers and native load
	50 MW

	Expected net flow next hour on constrained facility
	1000 MW

	Amount of interchange transactions using point-to-point transmission service to hold for reallocation
	1000 MW – 800 MW = 200 MW

	Amount to enter into IDC for interchange transactions using point-to-point transmission service
	950 MW – 200 MW = 750 MW


Example 3

	Flow to maintain on constrained facility
	800 MW

	Expected flow next hour from interchange transactions using point-to-point transmission service
	950 MW

	Contribution to flow next hour from service to network customers and native load
	-200 MW

	Expected net flow next hour on constrained facility
	750 MW

	Amount of interchange transactions using point-to-point transmission service to hold for reallocation
	750 MW – 800 MW = -50 MW

None are held


For a TLR levels 3b or 5b the IDC will request the reliability coordinator to provide the MW requested relief amount on the constrained facility, and will not present the current and next hour MW impact of point-to-point interchange transactions.  The reliability coordinator-entered requested relief amount will be used by IDC to determine the interchange transaction curtailments and flows due to service to network customers and native load (TLR Level 5b) in order to reduce the SOL or IROL violation on the constrained facility by the requested amount. 

IDC Calculations and Reporting 

At the time the TLR report is processed, the IDC will use all candidate interchange transactions for reallocation that met the approved tag submission deadline for reallocation plus those interchange transactions that were curtailed or halted on the previous TLR action of the same TLR event. The IDC will calculate and present an interchange transactions halt/curtailment list that will include reload and reallocation of interchange transactions.  The interchange transactions are prioritized as follows:

1. All interchange transactions will be arranged by transmission service priority according to the constrained path method. These priorities range from 1 to 6 for the various non-firm transmission service products (TLR levels 3a and 3b). interchange transactions using firm transmission service (priority 7) are used only in TLR levels 5a and 5b.  Next-hour market service is included at priority 0 (zero) 

2. In a TLR Level 3a the interchange transactions using non-firm transmission service in a given priority will be further divided into four sub-priorities, based on current schedule, current active schedule (identified by the submittal of a tag ADJUST message), next-hour schedule, and tag status. Solely for the purpose of identifying which interchange transactions to be loaded under a TLR 3a, various MW levels of an interchange transaction may be in different sub-priorities. The sub-priorities are shown in the table on the following page, and examples of interchange transactions using non-firm transmission service sub-priority settings are shown in the Transaction Sub-priority Examples section below.
	Sub-Priority
	Purpose
	Explanation and Conditions

	S1
	To allow a flowing interchange transaction to maintain or reduce its current MW amount in accordance with its energy profile.
	The MW amount is the lowest between currently flowing MW amount and the next-hour schedule.  The currently flowing MW amount is determined by the e-tag ENERGY PROFILE and ADJUST tables.  If the calculated amount is negative, zero is used instead.

	S2
	To allow a flowing interchange transaction that has been curtailed or halted by TLR to reload to the lesser of its current-hour MW amount or next-hour schedule in accordance with its energy profile. 
	The interchange transaction MW amount used is determined through the e-tag ENERGY PROFILE and ADJUST tables.  If the calculated amount is negative, zero is used instead.

	S3
	To allow a flowing interchange transaction to increase from its current-hour schedule to its next-hour schedule in accordance with its energy profile. 
	The MW amount used in this sub-priority is determined by the e-tag ENERGY PROFILE table.  If the calculated amount is negative, zero is used instead.

	S4
	To allow an interchange transaction that had never started and was submitted to the tag authority after the TLR (level 2 or higher) has been declared to begin flowing (i.e., the interchange transaction never had an active MW and was submitted to the IDC after the first TLR Action of the TLR event had been declared.) 
	The interchange transaction would not be allowed to start until all other interchange transactions submitted prior to the TLR with the same priority have been (re)loaded.  The MW amount used in this sub-priority is the next-hour schedule determined by the e-tag ENERGY PROFILE table.


3. All interchange transactions using firm transmission service will be put in the same priority group, and will be curtailed/reallocated pro-rata, independent of their current status (curtailed or halted) or time of submittal with respect to TLR issuance (TLR level 5a).  Under a TLR 5a, all interchange transactions using non-firm transmission service that are at or above the curtailment threshold will have been curtailed and hence sub-prioritizing is not required.

Assignment of Interchange Transaction Status

All interchange transactions processed in a TLR are assigned one of the following statuses:

PROCEED:
The interchange transaction has started or is allowed to start to the next hour MW schedule amount.

CURTAILED:
The interchange transaction has started and is curtailed due to the TLR, or it had not started but it was submitted prior to the TLR being declared (level 2 or higher).

HOLD:
The interchange transaction had never started and it was submitted after the TLR being declared – the interchange transaction is held from starting next hour, or the interchange transaction had never started and it was submitted to the IDC after the approved tag submission deadline – the interchange transaction is to be held from starting next hour and is not included in the reallocation calculations until following hour.

Upon acceptance of the TLR interchange transaction reallocation/reloading report by the issuing reliability coordinator, the IDC will generate a report to be sent to NERC that will include the PSE name and Tag ID of each interchange transaction in the IDC TLR report. The interchange transaction will be ranked according to its assigned status of HOLD, CURTAILED or PROCEED.  The reloading/reallocation report will be made available at NERC’s public TLR site, and it is NERC’s responsibility to format and publish the report. 

Tag Reloading for TLR Levels 1 and 0

When a TLR Level 1 or 0 is issued, the constrained facility is no longer under SOL or IROL violation, and all interchange transactions are allowed to flow.  In order to provide the reliability coordinators with a view of the interchange transactions that were halted or curtailed on previous TLR actions (level 2 or higher), and are now available for reloading, the IDC provides such information in the TLR report. 

New Tag Alarming

Those interchange transactions that are at or above the curtailment threshold and are not candidates for reallocation because the tags for those interchange transactions were not submitted by the approved tag submission deadline for reallocation will be flagged as HOLD and must not be permitted to start or increase during the next hour.  To alert reliability coordinators of those interchange transactions required to be held, the IDC will generate a report (for viewing within the IDC only) at various times.  The report will include a list of all HOLD interchange transactions.  In order not to overwhelm the reliability coordinator with alarms, only those who issued the TLR and those whose interchange transactions sink within their reliability area will be alarmed.  An alarm will be issued for a given tag only once and will be issued for all TLR levels for which halting of new interchange transactions is required: TLR Levels 2, 3a, 3b, 5a and 5b.

Tag Adjustment

The interchange transactions with statuses of HOLD, CURTAILED or PROCEED must be adjusted by a tag authority or tag approval entity. Without the tag adjustments, the IDC will assume that interchange transactions were not curtailed/held and are flowing at their specified schedule amounts. 

1. Interchange transactions marked as CURTAILED should be adjusted to a cap equal to, or at the request of the originating PSE, less than the reallocated amount (shown as the MW CAP on the IDC report). This amount may be zero if the interchange transaction is fully curtailed.

2. Interchange transactions marked as PROCEED should be adjusted to reload (NULL or to its MW level in accordance with its energy profile in the adjusted MW in the tag) if the interchange transaction has been previously adjusted; otherwise, if the interchange transaction is flowing in full, the tag authority need not issue an adjust.

3. Interchange transactions marked as HOLD should be adjusted to 0 MW.

Special Tag Status

There are cases in which a tag may be marked with a composite state of ATTN_REQD to indicate that tag authority/approval failed to communicate or there is an inconsistency between the validation software of different tag authority/approval entities.  In this situation, the tag is no longer subject to passive approval and its status change to IMPLEMENT may take longer than 10 minutes.  Under these circumstances, the IDC may have a tag that is issued prior to the tag submittal deadline that will not be a candidate for reallocation.  Such tags, when approved by the tag authority, will be marked as HOLD and must be halted. 

Transaction Sub-Priority Examples

The following describes examples of interchange transactions using non-firm transmission service sub-priority setting for an interchange transaction under different circumstances of current-hour and next-hour schedules and active MW flowing as modified by tag adjust table in e-tag. 

[image: image8.emf]00:00 01:00 02:00

:25 :25

IDC results prior

to 00:25 and

01:25 are

not distributed

Example 1 – Interchange transaction curtailed, next-hour energy profile is higher

	Energy profile: current hour
	20 MW

	Actual flow following curtailment: current hour
	10 MW

	Energy profile: next hour
	40 MW

	Sub-priorities for Interchange Transaction (MW)

	Sub-Priority
	MW Value
	Explanation

	S1
	10 MW
	Maintain current curtailed flow

	S2
	+10 MW
	Reload to current hour energy profile

	S3
	+20 MW
	Load to next hour energy profile

	S4
	


Example 2 – Transaction curtailed, next-hour energy profile is lower

	Energy profile: current hour
	40 MW

	Actual flow following curtailment: current hour
	10 MW

	Energy profile: next hour
	20 MW


[image: image9.wmf]MW

Time

10

20

40

S3

TLR

Tag


	Sub-priorities for Interchange Transaction (MW)

	Sub-Priority
	MW Value
	Explanation

	S1
	10 MW
	Maintain current curtailed flow

	S2
	+10 MW
	Reload to lesser of current and next-hour energy profile

	S3
	+0 MW
	Next-hour energy profile is 20MW, so no change in MW value

	S4
	


[image: image10.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Firm Transactions

must be submitted

to IDC by 00:25 to

start as scheduled

TLR 3b

IDC issues Congestion

Management Report

based on time of calling

TLR 3b. ADJUST List

follows.

IDC checks for

additional approved

Firm Transactions.

Congestion

Management Report

and second ADJUST

List issued if needed.

TLR 3a

Firm Transactions

that were held are

allowed to start at

02:00

Firm

Transactions in

IDC by 00:25

allowed to start

as scheduled.

Example 3 – Transaction not curtailed, next-hour energy profile is higher

	Energy profile: current hour
	20 MW

	Actual flow following curtailment: current hour
	20 MW (no curtailment)

	Energy profile: next hour
	40 MW


	Sub-priorities for Interchange Transaction (MW)

	Sub-Priority
	MW Value
	Explanation

	S1
	20 MW
	Maintain current flow (not curtailed)

	S2
	+0 MW
	Reload to lesser of current and next-hour energy profile

	S3
	+20 MW
	Next-hour energy profile is 40MW

	S4
	


[image: image11.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Firm Transactions

must be submitted

to IDC by start of

TLR 3b to start

TLR 3b

IDC issues

Congestion

Management

Report based on

time of calling

TLR 3b. ADJUST

List follows.

Firm Transactions

that are in the IDC

by start of TLR 3b

are started as

scheduled

Example 4 – Transaction not curtailed, next-hour energy profile is lower

	Energy profile: current hour
	40 MW

	Actual flow following curtailment: current hour
	40 MW (no curtailment)

	Energy profile: next hour
	20 MW


	Sub-priorities for Interchange Transaction (MW)

	Sub-Priority
	MW Value
	Explanation

	S1
	20 MW
	Reduce flow to next-hour energy profile (20MW)

	S2
	+0 MW
	Reload to lesser of current and next-hour energy profile

	S3
	+0 MW
	Next-hour energy profile is 20MW

	S4
	


Example 5 – TLR Issued before Interchange Transaction was scheduled to start

	Energy profile: current hour
	0 MW

	Actual flow following curtailment: current hour
	0 MW (interchange transaction scheduled to start after TLR initiated)

	Energy profile: next hour
	20 MW


[image: image12.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Firm Transactions

must be submitted

to IDC by 00:25 to

start as scheduled

Non-firm

Transactions are

Reallocated at

01:00.

TLR 3b

IDC issues

Congestion

Management

Report based on

time of calling TLR

3b. ADJUST List

follows.

IDC checks for

additional approved

Firm Transactions.

Congestion

Management Report

and second ADJUST

List issued if needed.

TLR 3a

Firm

Transactions are

started as

scheduled


	Sub-priorities for Interchange Transaction (MW)

	Sub-Priority
	MW Value
	Explanation

	S1
	0 MW
	Interchange transaction was not allowed to start

	S2
	+0 MW
	Interchange transaction was not allowed to start

	S3
	+20 MW
	Next-hour energy profile is 20MW

	S4
	+0
	Tag submitted prior to TLR


Section E: Interchange Transaction Curtailments During TLR Level 3b
This section provides the details for implementing TLR Level 3b, which curtail interchange transactions using non-firm point-to-point transmission service to assist the reliability coordinator to recover from SOL or IROL violations.  

The IDC shall issue ADJUST Lists to the Generation and Load Balancing Authorities and the Purchasing-Selling Entity who submitted the tag.  The ADJUST List will include: 

1. Interchange transactions using non-firm point-to-point transmission service that are to be curtailed or held during current and next hours.
2. Interchange transactions using firm point-to-point transmission service that were entered after 00:25 or issuance of TLR 3b (see Case 3 in Section F: Considerations for Interchange Transactions Using Firm Point-to-Point Transmission Service).

The sink balancing authority shall send the ADJUST lists back to the IDC as soon as possible to ensure the most accurate calculations for actions subsequent to the TLR 3b being called. 
[image: image13.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

Firm Transactions

must be submitted

to IDC by 00:25 to

start as scheduled

TLR 3b

IDC issues

Congestion

Management

Report based on

time of calling

TLR 3b. ADJUST

List follows.

IDC checks for

additional approved

Firm Transactions.

Congestion

Management Report

and second ADJUST

List issued if needed.

TLR 1

Firm

Transactions are

started as

scheduled. Non-

firm

Transactions

may be loaded.


The reliability coordinator shall be allowed to call a TLR Level 3a as soon as the SOL or IROL violation, which caused the TLR 3b to be called, has been mitigated. 

1. If the TLR Level 3a is called before the hour 01, then a reallocation shall be computed for the start of that hour.

2. Interchange transactions must be in the IDC by the approved tag submission deadline for reallocation (see Section D: Timing Requirements).
The Reliability Coordinator will no longer be required to call a TLR Level 3a as soon as the SOL or IROL violation that caused the TLR 3b to be called has been mitigated due to the inherent next hour Reallocation that takes place for the top of the next hour in the TLR Level 3b
Section F: Considerations for Interchange Transactions Using Firm Point-to-Point Transmission Service
The following cases explain the circumstances under which an interchange transaction using firm point-to-point transmission service will be allowed to start as scheduled during a TLR 3b:

[image: image14.emf]00:00

01:00

Beginning of

Next Hour

00:20 00:10

00:30

00:40 00:50

00:25

Beginning of

Current Hour

TLR 3b

IDC issues

Congestion

Management

Report based on

time of calling

TLR 3b. ADJUST

List follows.

Firm Transactions

that are in IDC by

00:25 may start as

scheduled

Firm Transactions

must be submitted

to IDC by 00:25 to

start as scheduled

TLR 2 or higher

Case 1: TLR 3b is called between 00:00 and 00:25 and the Interchange Transaction using Firm Point-to-Point Transmission Service is submitted to IDC by 00:25.

1. The IDC will examine the current hour (00) and next hour (01) for all Interchange Transactions.

2. The IDC will issue an ADJUST List based upon the time the TLR 3b is called.  The ADJUST List will include curtailments of Interchange Transactions using Non-firm Point-to-Point Transmission Service as necessary to allow room for those Interchange Transactions using Firm Point-to-Point Transmission Service to start as scheduled.

3. At 00:25, the IDC will check for additional Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC by that time and issue a second ADJUST List if those additional Interchange Transactions are found.  At 00:25, a reallocation will be performed to maintain the desired flow at the top of the following hour.
4. Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC by 00:25 will be allowed to start as scheduled.

5. Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC after 00:25 will be held.

6. Once the SOL or IROL violation is mitigated, the Reliability Coordinator shall call a TLR Level 3a (or lower). If a TLR Level 3a is called:

a. Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC by 00:25 will be allowed to start as scheduled at 02:00.

b. Interchange Transactions using Non-firm Point-to-Point Transmission Service that were held may then be reallocated to start at 02:00.
Case 2: TLR 3b is called after 00:25 and the Interchange Transaction using Firm Point-to-Point [image: image15.emf]00:00 01:00

01:25

Approved-Tag

Submission

Deadline for

Reallocation

Period

for initiating TLR 3A

for Reallocation at start

of next  hour

02:00

00:40

Transmission Service is submitted to the IDC no later than the time at which the TLR 3b is called.

1. The IDC will examine the current hour (00) and next hour (01) for all Interchange Transactions.

2. The IDC will issue an ADJUST List at the time the TLR 3b is called.  The ADJUST List will include additional curtailments of Interchange Transactions using Non-firm Point-to-Point Transmission Service as necessary to allow room for those Interchange Transactions using Firm Point-to-Point Transmission Service to start at as scheduled.

3. After 00:25, non-firm interchange transactions will be curtailed to meet the desired current hour relief and a reallocation will be performed to maintain the target flow identified for the current hour.
4. Interchange Transactions using Firm Point-to-Point Transmission Service that were submitted to the IDC by the time the TLR 3b was called will be allowed to start at as scheduled.

5. Interchange Transaction using Firm Point-to-Point Transmission Service that were submitted to the IDC after the TLR 3b was called will be held until the next issuance for TLR (either TLR 3b, 3a, or lower level).

Case 3. TLR 2 or higher is in effect, a TLR 3b is called after 00:25, and the Interchange Transaction using Firm Point-to-Point Transmission Service is submitted to the IDC by 00:25.


If a TLR 2 or higher has been issued and 3B is subsequently issued, then only those Interchange Transactions using Firm Point-to-Point Transmission Service that had been submitted to the IDC by 00:25 will be allowed to start as scheduled. All other Interchange Transactions are held.

Case 4. TLR 3b is called before 00:25 and the Interchange Transaction is submitted to the IDC by 00:25. TLR 3a is called at 00:40.


1. Same as Case 1, but TLR Level 3b ends at 00:40 and becomes TLR Level 3a.

2. All Interchange Transactions using Firm Point-to-Point Transmission Service will start as scheduled if in by the time the 3A is declared.

3. All Interchange Transactions using Non-firm Point-to-Point Transmission Service are reallocated at 01:00.
Case 5. TLR 3b is called before 00:25 and the Interchange Transaction is submitted to the IDC by 00:25. TLR 1 is called at 00:40.


1. Same as Case 1, but TLR Level 3b ends at 00:40 and becomes TLR Level 1.

2. All Interchange Transactions using Firm Point-to-Point Transmission Service will start as scheduled.

3. All Interchange Transactions using Non-firm Point-to-Point Transmission Service may be loaded immediately.

Section G: IDC Treatment of TLR Level 6
In order for all reliability coordinators to understand how the IDC handles the issuance of a TLR Level 6 this section describes the IDC functionality that currently exists and options that the reliability coordinator has when declaring this critical TLR Level. This will help ensure the correct action is taken for the given event.

When a reliability coordinator issues a TLR Level 6 on a flowgate in the IDC, the application will search the non-firm and firm tags that are in the IDC database for those that affect the flowgate greater than or equal to 5%.  It will create two sets of tags from this list for the reliability coordinator to curtail:

1. If the tag has an active MW amount in the current hour it will be curtailed to zero MW. 

2. If the tag is planned to start the next hour it will not be allowed to start and will be curtailed to zero for the next hour.

Once this report is created and displayed as the congestion management report, the reliability coordinator will then have three options to move forward with the TLR Level 6:

1. Confirm the curtailment list that contains the non-firm and firm complete curtailments for the current and next hour. 

1.1. This will alert the other reliability coordinators that a TLR Level 6 has been declared and that there are curtailments that need to be acknowledged for implementation.

1.2. Once the sinking reliability coordinators acknowledge the curtailments the IDC will send a reliability cap of zero to the balancing authorities on the tags for curtailment implementation.

2. Exclude some or all of the tag curtailments from the congestion management report before declaring a TLR Level 6.

2.1. This can be done by the issuing reliability coordinator using the “Re-issue/Exclude” option in the congestion management report.

2.2. This will give the issuing reliability coordinator the option of selecting those transactions they wish to exclude from the TLR issuance. 

2.3. Once the appropriate tags are selected the reliability coordinator will re-issue the TLR and the list of excluded tags will appear on the congestion management report, but will not be in the curtailed state.  The reliability coordinator will then have to confirm the TLR to send the TLR Level 6 notification to the other reliability coordinators.

2.4. Any tags that were not chosen for exclusion will be sent out to the other reliability coordinators for acknowledgement and curtailment.

2.5. This option allows the reliability coordinator to declare a TLR Level 6 without implementing tag curtailments.

3. Disregard some or all of the tag curtailments from the congestion management report while acknowledging the curtailments of a TLR Level 6:

3.1. The sinking reliability coordinator can only do this for each tag curtailment after they receive a TLR Level 6 congestion management report from the issuing reliability coordinator.

3.2. The sinking reliability coordinator will select the “Disregard” option for the tags they wish not to curtail.  This is done in the acknowledgement screen.

3.3. When the “Disregard” option is chosen and the “Acknowledgement” button selected the IDC will update the congestion management report to identify to all reliability coordinators that the sinking reliability coordinator has disregarded the curtailment and does not plan on implementing it.

3.4. This will prompt the issuing reliability coordinator to initiate a conversation with the sinking reliability cordinator for further clarification on why the suggested curtailment will not take place.

Section G - Comes from the RC reference document





This section was removed from IRO-006-3, but is still a valid functionality within the IDC.





Figure � SEQ Figure \* ARABIC �1� - Timeline showing Approved-tag Submission Deadline for Reallocation








Figure 5 - IDC report may be run prior to 00:25, but results are not distributed.









62
1

