[image: image1.png]0

I

0




North American Energy Standards Board

1301 Fannin, Suite 2350, Houston, Texas 77002

Phone:  (713) 356-0060, Fax:  (713) 356-0067, E-mail: naesb@naesb.org


Home Page: www.naesb.org

TO:
NAESB Wholesale Electric Quadrant Business Practices Subcommittee (BPS) and Interested Industry Participants

FROM: 
DeDe Kirby, Meeting/Project Manager, NAESB 

RE:
Final Minutes from the NAESB WEQ BPS Conference Call Meeting – August 21, 2006
DATE:

August 21, 2006
Wholesale Electric Quadrant
Business practices subcommittee conference call Meeting
August 21, 2006
final Minutes
1. Welcome and Administration
Ms. York welcomed the participants to the conference call meeting and Ms. Kirby gave the anti-trust advice.  Participants introduced themselves.  Ms. York stated the purpose of the meeting was to decide on how to progress with the Western Electric Coordinating Council (WECC) changes as stated in R06010. Mr. Saini moved to adopt the agenda and Ms. Perlman seconded the motion.  The agenda was adopted by consensus.        
2. Review R06010 and proposed motion
Ms. York clarified that the change to Manual Time Error Correction Version 0 standard (WEQBPS-006) requirement 5 was for the initiation column in the associated table (change to +/-5 seconds from +/- 2 seconds).  Ms. York asked if the change should also be made to the termination column.  Mr. Ashbaker confirmed that the change was not needed in the termination column of the table.  The following change was made to requirement 5:

006-5
Interconnection time monitoring. Each Interconnection Time Monitor shall monitor time error and shall initiate or terminate corrective action orders according to the following table: 

	Time (seconds)
	Initiation
	Termination

	
	East
	West
	ERCOT
	East
	West
	ERCOT

	Slow
	(10
	(5
	(3
	(6
	(0.5
	(0.5

	Fast
	+10
	+5
	+3
	+6
	(0.5
	(0.5


Mr. Ashbaker added that a minor change was also needed in requirement 4.  He stated that the time restriction concerning time error corrections for fast time did not apply to the Western Interconnection.  The following change was made to the requirement to state the exception:

006-4 
Time Error initiation. Time error corrections shall start and end on the hour or half-hour, and notice shall be given at least one hour before the time error correction is to start or stop. Time Error corrections shall last at least one hour, unless terminated by a Reliability Coordinator. Time Error corrections for fast time shall not be initiated between 0400-1100 Central Time, except for in the Western Interconnection. All Balancing Authorities within an Interconnection shall make all Time Error corrections directed by the Interconnection Time Monitor for its Interconnection. All Balancing Authorities within an Interconnection shall make Time Error Corrections at the same rate.

The subcommittee agreed that both changes to the standard were oversights by the subcommittee when the standard was originally drafted.  The subcommittee agreed the best method to make the changes was a minor correction.  
Mr. Schwermann moved to adopt the changes made to requirement 4 and 5 of WEQBPS-006.  Ms. Perlman seconded the motion.  The motion passed by consensus.  Ms. York will work with the NAESB office to draft the appropriate minor correction form.                    
3. Next Steps/Other Business
Ms. York stated that conference calls to continue work on R05004 (Develop transmission service request and scheduling standards using TTC/ATC/AFC and CBM/TRM) had been scheduled for September 7, 2006 and September 27, 2006.     
4. Adjourn
Mr. Schwermann moved to adjourn and Ms. Perlman seconded the motion.  The meeting was adjourned at 10:43 a.m. Central time by consent.
5. Attendance
	Last Name 
	First Name
	Organization

	Ashbaker
	Steve
	Western Electric Coordinating Council

	Badley
	Don
	Northwest Power Pool

	Gonzales
	Angela
	NAESB

	Kirby
	DeDe 
	NAESB

	Saini
	Narinder
	Entergy

	Schwermann
	Bob
	Sacramento Municipal Utility District

	York 
	Kathy 
	Tennessee Valley Authority


WEQ BPS Conference Call Meeting Final Minutes – 8/21/06 

Page 1

