Standard IRO-006-EI-1 — TLR Procedure for the Eastern Interconnection

A. Introduction

1. Title: Transmission Loading Relief Procedure for the Eastern Interconnection
2. Number: IRO-006-EI-1
3. Purpose:
To provide an Interconnection-wide transmission loading relief procedure for the Eastern Interconnection that can be used to prevent and/or manage potential or actual SOL and IROL violations to maintain reliability of the bulk electric system.
4. Applicability:

4.1. Reliability Coordinators in the Eastern Interconnection. 

5. Effective Date:
Effective upon BOT adoption
B. Requirements

Introduction 

A Reliability Coordinator (RC) in the Eastern Interconnection experiencing a potential or actual SOL or IROL violation within its Reliability Coordinator Area shall, with its authority and at its discretion, utilize one or more procedures to provide transmission loading relief.  These procedures can be a “local” (regional, interregional, or sub-regional) transmission loading relief procedure or the following Interconnection-wide procedure.  If a Reliability Coordinator in the Eastern Interconnection decides to use the Interconnection-wide Transmission Loading Relief (TLR) procedure to prevent and/or manage potential or actual SOL and IROL violations on transmission facilities, then that Reliability Coordinator shall comply with the requirements set forth below.  A Reliability Coordinator should not use the TLR procedure alone to mitigate an IROL violation, as it is an inappropriate and ineffective tool to mitigate an IROL violation due to the time required to implement the procedure.  Other acceptable and more effective procedures to mitigate actual IROL violations include: reconfiguration, redispatch, use of demand-side management, or load shedding.

INITIATING A TLR

R1. When initiating a TLR procedure, the Reliability Coordinator shall determine: [Violation Risk Factor: Medium] [ Time Horizon: Real-time Operations]
R1.1. The TLR level to prevent or mitigate a SOL or IROL violation in accordance with the criteria in Appendix A, and
R1.2. The required TLR relief actions needed to prevent or mitigate the SOL or IROL violation

R2. The Reliability Coordinator initiating a TLR on a transmission facility(ies) shall communicate the TLR levels and required relief actions to other entities by: [Violation Risk Factor: Medium] [ Time Horizon: Real-time Operations]
R2.1. Notifying all Reliability Coordinators in the Eastern Interconnection of the initiated TLR levels
R2.2. Communicating the required TLR relief actions to:

R2.2.1.  All Reliability Coordinators in the Eastern Interconnection, and 
R2.2.2. Those Reliability Coordinators in other Interconnections responsible for curtailing or reloading Interchange Transactions crossing Interconnection boundaries.  

R3. The Reliability Coordinator initiating a TLR on a transmission facility(ies) shall request that the following entities impacted by the relief actions implement the communicated relief actions: [Violation Risk Factor: Medium] [ Time Horizon: Real-time Operations]
R3.1. The RC in the EI associated with the Sink Balancing Authority in the EI of any Interchange Transactions being curtailed or reloaded

R3.2. The RC in the EI associated with those Balancing Authorities in the EI for which Network and Native Load relief is being requested

R3.3. The RC in the EI associated with those Market Operators in the EI for which Market Flow relief is being requested

R3.4. The RC in the EI associated with those Balancing Authorities in the EI operating the DC-Tie for an Interchange Transaction sinking outside the EI and crossing an interconnection boundary that has been requested to be curtailed or reloaded

R4. The Reliability Coordinator that has initiated a TLR shall manage the TLR event by: [Violation Risk Factor: Medium] [ Time Horizon: Real-time Operations]
R4.1. Updating the level of TLR as system conditions change by following the assessment process indicated in R1, above. 

R4.2. Updating any relief obligations at least once every hour. 
R4.3. Terminating the TLR event and revoking all preventive and mitigating TLR actions previously taken when the transmission facility(ies) is within the SOL and IROL and the projected transmission facility(ies)’s operating conditions with the preventive and mitigating actions revoked will not exceed the SOL or IROL or cause any other reliability concern for the current hour and next hour. 

RESPONDING TO TLR

R5. A Reliability Coordinator in the Eastern Interconnection responding to a TLR request (as described in R3) shall comply with the request for relief by taking one or more of the following actions: [Violation Risk Factor: Medium] [ Time Horizon: Real-time Operations]
R5.1. Implementing the communicated relief actions directed by the issuing RC as follows:

· Directing the Balancing Authorities under its purview to implement the Interchange Transaction change requests for which the Balancing Authorities are responsible. 

· Directing the Balancing Authorities under its purview to provide the Network and Native Load relief obligation for which the Balancing Authorities are responsible. 

· Directing the Market Operators under its purview to provide the Market Flow relief obligation for which the Market Operators are responsible 

R5.2. Implementing a relief procedure that has been pre-approved by the ERO for use by the responding Reliability Coordinator in lieu of some or all of the requested actions in R5.1, provided that its implementation is expected to provide the requested relief associated with the actions not taken in R5.1 and the initiating RC has been notified of the use of the procedure.
R5.3. Implementing alternate actions to those in R5.1 or R5.2 provided that

R5.3.1. Some or all of the actions in R5.1 or R5.2 are expected to result in a reliability concern or are expected to be ineffective, and
R5.3.2. The alternate actions have been agreed to by the initiating Reliability Coordinator, and

R5.3.3. The alternate actions are not expected to adversely affect reliability.  
R6. A Reliability Coordinator responding to a TLR event shall acknowledge to the initiating Reliability Coordinator the actions to be taken in response to the request for relief within thirty minutes of the request.  [Violation Risk Factor: Medium] [ Time Horizon: Real-time Operations]
C. Measures
M1. 
Each Reliability Coordinator shall be capable of providing evidence (such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or alarm program printouts) that they called the appropriate TLR level. (R1)

M2.
Each Reliability Coordinator shall be capable of providing evidence (such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or alarm program printouts) that when initiating TLR, they notified all other Reliability Coordinators in the Eastern Interconnection that a TLR had been initiated.( R2.1)

M3.
Each Reliability Coordinator shall be capable of providing evidence (such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or alarm program printouts) that when initiating TLR, they communicated the requested relief actions to all the other Reliability Coordinators. (R2.2)

M4.
Each Reliability Coordinator shall be capable of providing evidence (such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or alarm program printouts) that when initiating TLR, they requested all the Reliability Coordinators listed in R3.1, R3.2, R3.3, and R3.4 to take those actions. (R3)

M5.
Each Reliability Coordinator shall be capable of providing evidence (such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or alarm program printouts) that they managed the TLR levels in accordance with R4. (R4)

M6.
Each Reliability Coordinator shall be capable of providing evidence (such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or alarm program printouts) that they correctly implemented the actions described in R5. (R5)
M7.
Each Reliability Coordinator that uses a relief procedure in lieu of some or all of the requested actions in R5.1 shall be capable of providing evidence (such as formal approval letter or minutes of meeting) that the relief procedure has been pre-approved by the ERO. (R5.2)
M8.
Each Reliability Coordinator responding to a TLR event shall be capable of providing evidence (such as operator logs, voice recordings or transcripts of voice recordings, electronic communications, or alarm program printouts) that they acknowledged their actions with the initiating Reliability Coordinator. (R6)

D. Compliance

1.
Compliance Monitoring Process 

1.1.
Compliance Monitoring Responsibility:  The Regional Reliability Organization shall have responsibility for compliance monitoring.

1.2.
Compliance Monitoring Period and Reset Time Frame:  The compliance monitoring period shall be one (1) calendar year. The reset period shall be one (1) month without a violation.

1.3.
Data Retention 
	Measure
	Entity
	Data Retention Period

	M1
	RC
	12 months

	M2
	RC
	12 months

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	M3
	RC
	12 months

	M4
	RC
	12 months

	M5
	RC
	12 months

	M6
	RC
	The approved duration of the procedure in effect plus one calendar year thereafter.

	
	
	

	
	
	

	
	
	

	M7
	RC
	12 months

	M8
	RC
	12 months

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


2.
Additional Compliance Information:  Each Reliability Coordinator shall demonstrate compliance through self-certification submitted to its Compliance Monitor annually and reporting by exception. The Compliance Monitor may also use scheduled on-site reviews every three years, and investigations upon complaint, to assess performance. Each Reliability Coordinator shall have the following available for its Compliance Monitor to inspect during a scheduled, on-site review or within 5 days of a request as part of an investigation upon complaint:

2.1.
Operations logs, voice recordings or transcripts of voice recordings or other documentation providing the evidence of its compliance to all the requirements for all Interconnection-wide procedures that it has implemented during the review period.

2.2.
TLR reports.

3. Violation Severity Levels 

	R #
	Lower VSL
	Moderate
	High VSL
	Severe VSL

	R1.
	
	
	The Reliability Coordinator did not apply the criteria in Appendix A in determining the TLR Level, or could not demonstrate the need to deviate from following these criteria for reliability reasons,

OR

The Reliability Coordinator did not determine the required relief actions needed to prevent or mitigate the SOL or IROL violation.
	The Reliability Coordinator did not apply the criteria in Appendix A in determining the TLR Level, or could not demonstrate the need to deviate from following these criteria for reliability reasons,
AND

The Reliability Coordinator did not determine the required relief actions needed to prevent or mitigate the SOL or IROL violation.

	R2.
	The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not notify to 1 to 2 Reliability Coordinators in the Eastern Interconnection that a TLR has been initiated. 
OR
The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not communicate the required relief to 1 to 2 Reliability Coordinators in the Eastern Interconnection.


	The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not notify to 3 to 4 Reliability Coordinators in the Eastern Interconnection that a TLR has been initiated.
OR
The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not communicate the required relief to 3 to 4 Reliability Coordinators in the Eastern Interconnection.


	The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not notify to 5 to 6 Reliability Coordinators in the Eastern Interconnection that a TLR has been initiated.
OR
The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not communicate the required relief to 5 to 6 Reliability Coordinators in the Eastern Interconnection.


	The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not notify to 7 or more Reliability Coordinators in the Eastern Interconnection that a TLR has been initiated.
OR
The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not communicate the required relief to 7 or more Reliability Coordinators in the Eastern Interconnection. 

OR
The Reliability Coordinator initiating a TLR on a transmission facility(ies) did not communicate the required relief to one or more Reliability Coordinators in other Interconnections responsible for curtailing or reloading Interchange Transactions crossing Interconnection boundaries.  



	R3
	The Reliability Coordinator initiating a TLR on a transmission facility(ies) requested 75% or more of those responding RCs impacted by the relief actions to implement the communicated relief actions. 
	The Reliability Coordinator initiating a TLR on a transmission facility(ies) requested more than 50%, but not more than 75%, of those responding RCs impacted by the relief actions to implement the communicated relief actions.
	The Reliability Coordinator initiating a TLR on a transmission facility(ies) requested more than 25%, but not more than 50% or more of those responding RCs impacted by the relief actions to implement the communicated relief actions.
	The Reliability Coordinator initiating a TLR on a transmission facility(ies) requested 25% or less of those responding RCs impacted by the relief actions to implement the communicated relief actions.

	R4
	
	The Reliability Coordinator initiating a TLR did not terminate the TLR event and revoke all preventive and mitigating TLR actions previously taken when the transmission facility(ies) was within the SOL and IROL and the projected transmission facility(ies)’s operating conditions with the preventive and mitigating actions revoked did not exceed the SOL or IROL or cause any other reliability concern for the current hour and next hour.
	The Reliability Coordinator initiating a TLR did not update the level of TLR as system conditions change by following the assessment process indicated in R1

OR
The Reliability Coordinator initiating a TLR did not update any relief obligations at least once every hour.
	The Reliability Coordinator initiating a TLR did not update the level of TLR as system conditions change by following the assessment process indicated in R1, and did not  update any relief obligations at least once every hour.

	R5
	N/A
	N/A
	When complying with the request for relief, the responding Reliability Coordinator who chose to implement the communicated relief actions directed by the issuing Reliability Coordinator followed some but not all the steps listed in R5.1 as directed.
OR
When complying with the request for relief, the responding Reliability Coordinator who chose not to implement some or all the communicated relief actions as directed by the issuing Reliability Coordinator, and implemented a relief procedure to provide the relief but the procedure had not been pre-approved by the ERO for use by the responding Reliability Coordinator in lieu of some or all of the requested actions in R5.1.

OR
The responding Reliability Coordinator chose to implement alternative actions not listed in 5.1 or 5.2, but such actions had not received prior agreement by the initiating Reliability Coordinator.
	When requested to comply with the request for relief, the responding Reliability Coordinator did not implement any of the actions listed R5.1 to R5.3

	R6
	The Reliability Coordinator responding to a TLR event did acknowledge to the initiating Reliability Coordinator the actions that had been taken in response to the request for relief but the acknowledgement was made more than thirty minutes after the request but not more than one hour after the request.
	The Reliability Coordinator responding to a TLR event did acknowledge to the initiating Reliability Coordinator the actions that had been taken in response to the request for relief but the acknowledgement was made more than one hour after the request but not more than two hours after the request.
	The Reliability Coordinator responding to a TLR event did acknowledge to the initiating Reliability Coordinator the actions that had been taken in response to the request for relief but the acknowledgement was made more than two hours after the request but not more than three hours after the request.
	The Reliability Coordinator responding to a TLR event did acknowledge to the initiating Reliability Coordinator the actions that had been taken in response to the request for relief but the acknowledgement was made more than three hours after the request 

OR

The Reliability Coordinator responding to a TLR event did not acknowledge to the initiating Reliability Coordinator the actions that had been taken in response to the request for relief.


E. Regional Differences 

1. PJM/MISO Enhanced Congestion Management (Curtailment/Reload/Reallocation) Waiver approved March 25, 2004.  

2. Southwest Power Pool (SPP) Regional Difference – Enhanced Congestion Management (Curtailment/Reload/Reallocation).  The SPP regional difference, which is equivalent to the PJM/MISO waiver, shall apply within the SPP region as follows:

This regional difference impacts actions on behalf of those SPP Balancing Authorities that are participating in the SPP market.  This regional difference does not impact those Balancing Authorities for which SPP will continue to act as the Reliability Coordinator but that are not participating in the SPP market.

SPP shall calculate the impacts of SPP market flow on all facilities included in SPP’s Coordinated Flowgate List.  SPP shall conduct sensitivity studies to determine which external flowgates (outside SPP’s footprint) are significantly impacted by the market flows of SPP’s control zones (currently the balancing areas that exist today in the IDC).  SPP shall perform studies to determine which external flowgates SPP will monitor and help control.  An external flowgate selected by one of the studies will be considered a Coordinated Flowgate (CF).

In its calculation, SPP shall consider market flow impacts as the impacts of energy dispatched by the SPP market and self-dispatched energy serving load in the market footprint, but not tagged.  SPP shall use a method equivalent to the PJM/MISO Market Flow Calculation methodology identified in the PJM/MISO waiver.  Impacts of tagged transactions representing delivery of energy not dispatched by the SPP market and energy dispatched by the market but delivered outside the footprint will not be included in market flow.

SPP shall separate the market flow impacts for current hour and next hour into their appropriate priorities and shall provide those market flow impacts to the IDC.  The market flows will be represented in the IDC and made available for curtailment under the appropriate TLR Levels.  The market flow impacts will not be represented by conventional interchange transaction tags.

The SPP method will impact the following sections of the TLR Procedure:

Network and Native Load (NNL) Calculations ( The SPP regional difference modifies Attachment 1-IRO-006-1 Section 5 “Parallel Flow Calculation Procedure for Reallocating or Curtailing Firm Transmission Service” within the SPP region.

Section 5 of Attachment 1-IRO-006-1 requires that the “Per Generator Method without Counter Flow” methodology be utilized to calculate the portion of parallel flows on any Constrained Facility due to Network Integration (NI) transmission service and service to Native Load (NL) of each balancing authority.

SPP shall use a “Market Flow Calculation” methodology to calculate the portion of parallel flows on all facilities included in the RTO’s “Coordinated Flowgate List” due to NI service or service to NL of each balancing authority.

The Market Flow Calculation differs from the Per Generator Method in the following ways:

· The contribution from all market area generators will be taken into account.

· In the Per Generator Method, only generators having a GLDF greater than 5% are included in the calculation.  Additionally, generators are included only when the sum of the maximum generating capacity at a bus is greater than 20 MW.  The market flow calculations will use all positively impacting flows down to 0% with no threshold.  Counter flows will not be included in the market flow calculation. 

· The contribution of all market area generators is based on the present output level of each individual unit.

· The contribution of the market area load is based on the present demand at each individual bus.

By expanding on the Per Generator Method, the market flow calculation evolves into a methodology very similar to the “Per Generator Method” method, while providing increased Interchange Distribution Calculator (IDC) granularity.  Counter flows are also calculated and tracked in order to account for and recognize that the either the positive market flows may be reduced or counter flows may be increased to provide appropriate relief on a flowgate. 

These NNL values will be provided to the IDC to be included and represented with the calculated NNL values of other Balancing Authorities for the purposes of identifying and obtaining required NNL relief across a flowgate in congestion under a TLR Level 5A/5B. 

Pro Rata Curtailment of Non-Firm Market Flow Impacts ( The SPP regional difference modifies Attachment 1-IRO-006-1 Appendix B “Transaction Curtailment Formula” within the SPP region.

Appendix B “Transaction Curtailment Formula” details the formula used to apply a weighted impact to each non-firm tagged Interchange Transaction (Priorities 1 thru 6) for the purposes of Curtailment by the IDC.  For the purpose of Curtailment, the non-firm market flow impacts (Priorities 2 and 6) submitted to the IDC by SPP should be curtailed pro-rata as is done for Interchange Transaction using firm transmission service. This is because several of the values needed to assign a weighted impact using the process listed in Appendix B will not be available:

· Distribution Factor (no tag to calculate this value from)

· Impact on Interface value (cannot be calculated without Distribution Factor)

· Impact Weighting Factor (cannot be calculated without Distribution Factor)

· Weighted Maximum Interface Reduction (cannot be calculated without Distribution Factor)

· Interface Reduction (cannot be calculated without Distribution Factor)

· Transaction Reduction (cannot be calculated without Distribution Factor)

While the non-firm market flow impacts submitted to the IDC are to be curtailed pro rata, the impacting non-firm tagged Interchange Transactions could still use the existing processes to assign the weighted impact value.

Assignment of Sub-Priorities ( The SPP regional difference modifies Attachment 1-IRO-006-1 Appendix E “How the IDC Handles Reallocation”, Section E2 “Timing Requirements”, within the SPP region.

Under the header “IDC Calculations and Reporting” in Section E2 of Appendix E to Attachment 1-IRO-006-1, the following requirement exists: “In a TLR Level 3a the Interchange Transactions using Non-firm Transmission Service in a given priority will be further divided into four sub-priorities, based on current schedule, current active schedule (identified by the submittal of a tag ADJUST message), next-hour schedule, and tag status.  Solely for the purpose of identifying which Interchange Transactions to be loaded under a TLR 3a, various MW levels of an Interchange Transaction may be in different sub-priorities.  The sub-priorities are shown in the following table:

	Priority
	Purpose
	Explanation and Conditions

	S1
	To allow a flowing Interchange Transaction to maintain or reduce its current MW amount in accordance with its energy profile.
	The MW amount is the lowest between currently flowing MW amount and the next-hour schedule. The currently flowing MW amount is determined by the e-tag ENERGY PROFILE and ADJUST tables. If the calculated amount is negative, zero is used instead.

	S2
	To allow a flowing Interchange

Transaction that has been curtailed or halted by TLR to reload to the lesser of its current-hour MW amount or next-hour schedule in accordance with its energy profile.
	The Interchange Transaction MW amount used is determined through the e-tag ENERGY PROFILE and ADJUST tables. If the calculated amount is negative, zero is used instead.

	S3
	To allow a flowing Transaction to increase from its current-hour schedule to its next-hour schedule in accordance with its energy profile.
	The MW amounts used in this sub-priority is determined by the e-tag ENERGY PROFILE table. If the calculated amount is negative, zero is used instead.

	S4
	To allow a Transaction that had never started and was submitted to the Tag Authority after the TLR (level 2 or higher) has been declared to begin flowing (i.e., the Interchange Transaction never had an active MW and was submitted to the IDC after the first TLR Action of the TLR Event had been declared.)
	The Transaction would not be allowed to start until all other Interchange Transactions submitted prior to the TLR with the same priority have been (re)loaded. The MW amount used is the sub-priority is the next-hour schedule determined by the e-tag ENERGY PROFILE table.


SPP shall use a “Market Flow Calculation” methodology to calculate the amount of energy flowing across all facilities included in the RTO’s “Coordinated Flowgate List” that is associated with the operation of the SPP market.  This energy is identified as “market flow.”

These market flow impacts for current hour and next hour will be separated into their appropriate priorities and provided to the IDC by SPP.  The market flows will then be represented and made available for curtailment under the appropriate TLR Levels.

Even though these market flow impacts (separated into appropriate priorities) will not be represented by conventional “tags,” the impacts and their desired levels will still be provided to the IDC for current hour and next hour.  Therefore, for the purposes of reallocation, a sub-priority (S1 thru S4) should be assigned to these market flow impacts by the NERC IDC as follows, using comparable logic as would be used if the impacts were in fact tagged transactions. 

	Priority
	Purpose
	Explanation and Conditions

	S1
	To allow existing market flow to maintain or reduce its current MW amount.
	The currently flowing MW amount is the amount of market flow existing after the RTO has recognized the constraint for which TLR has been called. If the calculated amount is negative, zero is used instead.

	S2
	To allow market flow that has been curtailed or halted by TLR to reload to its desired amount for the current-hour.
	This is the difference between the current hour unconstrained market flow and the current market flow.  If the current-hour unconstrained market flow is not available, the IDC will use the most recent market flow since the TLR was first issued or, if not available, the market flow at the time the TLR was fist issued.

	S3
	To allow a market flow to increase to its next-hour desired amount.
	This is the difference between the next hour and current hour unconstrained market flow.


F. Associated Documents

G. Revision History

	Version 
	Date 
	Action 
	Tracking 

	0 
	4/1/2005 
	Effective Date 
	New 

	0 
	8/8/2005 
	Removed “Proposed” from Effective Date 
	Errata 

	1 
	8/8/2005 
	Revised Attachment 1 
	Revision 

	3 
	2/26/2007 
	Revised Purpose and Attachment 1 related to NERC NAESB split of the TLR procedure 
	Revision 

	4
	
	NERC/NAESB split of Attachment 1with the intention of making minimal changes to the remaining content & format
	Revision 

	5 
	
	Rewrite of Attachment 1 following NERC/NAESB split to improve clarity and organization
	Revision 


Appendix A

The following criteria are intended to assist the RC in determining what level of TLR to call.  However, the RC has the discretion to choose any of these levels regardless of the criteria listed below, provided the RC has reliability reasons to take such action.  

	Level
	System Condition

	TLR-1
	· One or more transmission facilities are expected to approach or exceed their SOL or IROL within 8 hours.

	TLR-2
	· One or more transmission facilities are approaching or at their SOL or IROL. 

· It is expected that exceeding SOLs and IROLs can be avoided through holding new and increasing non-firm transactions and energy flows for the next hour.

	TLR-3a
	· One or more transmission facilities are expected to exceed their SOL or IROL within the next-hour.

· It is expected that exceeding SOLs and IROLs can be avoided through full or partial curtailment or reallocation of non-firm transactions and energy flows.

	TLR-3b
	· One or more transmission facilities are exceeding their SOL or IROL, or

· One or more transmission facilities are expected to exceed their SOL or IROL within the current hour.

· It is expected that exceeding SOLs and IROLs can be avoided through full or partial curtailment or reallocation of non-firm transactions and energy flows.

	TLR-4
	· One or more transmission facilities are expected to exceed their SOL or IROL.

· It is expected that exceeding SOLs and IROLs can be avoided through 

· Full curtailment of non-firm transactions, and energy flows, and

· Reconfiguration of the transmission system.

	TLR-5a
	· One or more transmission facilities are expected to exceed their SOL or IROL when the next-hour’s transactions start.

· It is expected that exceeding SOLs and IROLs can be avoided through 

· Full curtailment non-firm transactions and energy flows

· Reconfiguration of the transmission system, and

· Full or partial curtailment or reallocation of firm transactions and energy flows.

	TLR-5b
	· One or more transmission facilities are exceeding their SOL or IROL, or

· One or more transmission facilities are expected to exceed their SOL or IROL within the current hour.

· It is expected that exceeding SOLs and IROLs can be avoided through 

· Full curtailment non-firm transactions and energy flows

· Reconfiguration of the transmission system, and

· Full or partial curtailment of firm transactions and energy flows.


1 and 2 to be retired upon completion of the Phase 2 field test -  in the interim the Regional Difference will be contained in both the NERC and NAESB standards.





Ben’s note: Added M7 to address the ERO approved procedure requirement. 











Ben’s note: this change is required to take care of subrequirement R2.2.2.








�Based on NOPR, suggest adding this language.





Draft 1: June xx, 2008

Page 1 of 16 


