## Sheet1
Generator Owner & Generator Operator
NERC Requirement | Language | WEQ BPS Comments
R1 | At least once every five calendar years, each Generator Owner shall, for each of its applicable generating unit(s): [Violation Risk Factor: Lower] [Time Horizon: Long-term Planning] | 9/19/24 - WEQ BPS reviewed and determined that this is a requirement for the generator owner to maintain its own information. Business practices are not needed
R1.1 | Calculate the Extreme Cold Weather Temperature for each of its applicable unit(s) and identify the calculation date and source of temperature data; and
R1.1.1 | If the re-calculated Extreme Cold Weather Temperature is lower than the previous Extreme Cold Weather Temperature, the entity shall review and update its cold weather preparedness plan(s) under Requirement R4 within six (6) months of the recalculation. If new corrective actions are needed to provide the required operational capability under Requirement R2 or R3, the entity shall develop a Corrective Action Plan within 6 months of the recalculation.
R1.2 | Identify generating unit(s) cold weather data, to include:
R1.2.1 | Generating unit(s) operating limitations in cold weather to include:
R1.2.1.1 | Capability and availability;
R1.2.1.2 | Fuel supply and inventory concerns;
R1.2.1.3 | Start-up issues;
R1.2.1.4 | Fuel switching capabilities; and
R1.2.1.5 | Environmental constraints.
R1.2.2 | Generating unit(s) minimum: • Design temperature, and if available, the concurrent wind speed and precipitation; • Historical operating temperature at least one hour in duration, and if available, the concurrent wind speed and precipitation; or • Current cold weather performance temperature determined by an engineering analysis, which includes the concurrent wind speed and precipitation.
M1 | Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation and design information, operating data, or engineering analysis that supports its generating unit minimum temperature.
R2 | Applicable to generating units with a commercial operation date on or after October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius),1 shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] | 9/19/24 - WEQ BPS reviewed and determined that this is a requirement for the generator owner to maintain its own information. Business practices are not needed
Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the unit(s)’ Extreme Cold Weather Temperature with sustained concurrent twenty (20) mph wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours; or
Develop a Corrective Action Plan(s) to add new or modify existing or previously planned freeze protection measures to provide the capability to operate at the unit(s)’ Extreme Cold Weather Temperature with a sustained concurrent twenty (20) mph wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours.
M2 | Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its unit(s) in accordance with R2, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature under Requirement R1 Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s).
R3 | Applicable to generating unit(s) in commercial operation prior to October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius),2 shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] | 9/19/24 - WEQ BPS reviewed and determined that this is a requirement for the generator owner to maintain its own information. Business practices are not needed
Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the unit(s)' Extreme Cold Weather Temperature; or
Develop a Corrective Action Plan to add new or modify existing freeze protection measures to provide the capability to operate at the unit(s)' Extreme Cold Weather Temperature.
M3 | Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its unit(s) in accordance with R3, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include, but is not limited to, the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature per Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s).
R4 | Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum: [Violation Risk Factor: High] [Time Horizon: Operations Planning and Real-time Operations] | 9/19/24 - WEQ BPS reviewed and determined that this is a requirement for the generator owner to maintain its own information. Business practices are not needed
R4.1 | The lowest calculated Extreme Cold Weather Temperature for each unit, as determined in Requirement R1;
R4.2 | The generating unit cold weather data, as determined in Requirement R1.2;
R4.3 | Documentation identifying Generator Cold Weather Critical Components;
R4.4 | Documentation of freeze protection measures implemented on Generator Cold Weather Critical Components which includes measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain); and
R4.5 | Annual inspection and maintenance of generating unit(s) freeze protection measures.
M4 | Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation to demonstrate inspections and maintenance have been completed may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained.
R5 | Each Generator Owner in conjunction with its Generator Operator shall identify the entity responsible for providing the generating unit-specific training, and that identified entity shall provide annual training to its maintenance or operations personnel responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R4. [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning, Operations Planning] | 9/19/24 - WEQ BPS reviewed and determined that this is a requirement for the generator owner to maintain its own information. Business practices are not needed
M5 | Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed annual training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R5.
R6 | Each Generator Owner shall, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), develop a Corrective Action Plan when the generating unit experiences a Generator Cold Weather Reliability Event. The Corrective Action Plan shall be developed within 150 days or by July 1, whichever is earlier, and contain at a minimum: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] | 9/19/24 - WEQ BPS reviewed and determined that this is a requirement for the generator owner to maintain its own information. Business practices are not needed
R6.1 | A summary of the identified cause(s) for the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data;
R6.2 | A review of applicability to similar equipment at generating units owned by the Generator Owner; and
R6.3 | An identification of operating limitations or impacts to the cold weather preparedness plan that would apply until execution of the corrective action(s) identified in the Corrective Action Plan.
M6 | Each Generator Owner will have documented evidence that it developed a Corrective Action Plan following a Cold Weather Reliability Event at an applicable unit in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s) and updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan.
R7 | Each Generator Owner, for each Corrective Action Plan developed pursuant to Requirements R1, R2, R3, or R6, shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | 9/19/24 - WEQ BPS reviewed and determined that this is a requirement for the generator owner to maintain its own information. Business practices are not needed
R7.1 | Include a timetable for implementing the selected corrective action(s) that shall:
R7.1.1 | List the action(s) which address(es) existing equipment or freeze protection measures, if any, to be completed within 24 calendar months of completing development of the Corrective Action Plan;
R7.1.2 | List the action(s) which require(s) new equipment or freeze protection measures, if any, to be completed within 48 calendar months of completing development of the Corrective Action Plan; and
R7.1.3 | List the updates to the cold weather preparedness plan required under Requirement R4 to identify the updates or additions to the Generator Cold Weather Critical Components and their freeze protection measures;
R7.2 | Implement the Corrective Action Plan in accordance with the specified timetables in Requirement R7 Part 7.1;
R7.3 | Update the Corrective Action Plan action(s) and timetable(s), with justification, if corrective action(s) change or timetable(s) exceed the timelines in Requirement R7 Part 7.1; and
R7.4 | Document in a declaration, with justification, any Generator Cold Weather Constraint that precludes the Generator Owner from implementing selected action(s) contained within the Corrective Action Plan.
M7 | Each Generator Owner shall have dated evidence that demonstrates it implemented each Corrective Action Plan, including updating actions or timetables, or has explained in a declaration why corrective actions are not being implemented in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the implementation of each Corrective Action Plan and the completion of actions for each Corrective Action Plan including revision history of each Corrective Action Plan and, if applicable, justification to support any changes to corrective action(s) identified in the Corrective Action Plan or timetables exceeding the timelines in Requirement R7 Part 7.1. For each Corrective Action Plan applying to multiple generating units, the timetable shall reflect implementation at each unit addressed in the Corrective Action Plan. Evidence may also include work management program records, work orders, and maintenance records. Any declaration shall contain dated documentation to support constraints identified by the Generator Owner.
R8 | Each Generator Owner that creates a Generator Cold Weather Constraint declaration shall: [Violation Risk Factor: Medium] [Time Horizon: Long-term Planning] | 9/19/24 - WEQ BPS reviewed and determined that this is a requirement for the generator owner to maintain its own information. Business practices are not needed
R8.1 | Review the Generator Cold Weather Constraint declaration at least every five calendar years or as needed when a change of status to the Generator Cold Weather Constraint occurs; and
R8.2 | Update the operating limitations associated with capability and availability under Requirement R1 Part R1.2 if applicable.
M8 | Each Generator Owner shall have dated evidence that demonstrates it performed the review and updated operating limitations as needed. Acceptable evidence may include, but is not limited to the following dated documentation (electronic or hardcopy format): records that document the performance of the review and update to the operating limitations, as needed.